| Review of Valley View Sewer District 2011 Comprehensive Sewer Plan |
| --- |
| Service Area The Valley View Sewer District (District) owns and operates a municipal waste water collection system that is located south of the City of Seattle. The District generally extends from the City of Seattle limits at South Director Street and South Cambridge Street on the north to South 176th and 182nd Streets on the south, and from Interstate Highway 5 and State Route 599 on the east to 1st Avenue South and State Route 509 on the west. The District serves portions of the cities of Burien, SeaTac, Seattle, Tukwila, and unincorporated King County. The future service area of the District is slightly larger than the District’s corporate boundary, and its boundary is the logical area which could be served by Valley View based on topography and distance to existing system facilities. The District serves approximately 8,000 connections, or approximately 14,000 Equivalent Residential Units in an area of approximately 6,071 acres. These connections are served through a network of collector and interceptor lines ranging in size from 6 to 24 inches in diameter. There are approximately 120 miles of sanitary sewer lines and an estimated 30 miles of side sewers. The District holds two franchises; franchise numbers 6426 and 8671 for sewer service that expire January 6, 2011, and June 1, 2017, respectively. The County will initiate a franchise update process with the District to address franchise 6426. Reclaimed Water The District recognizes the value of reclaimed water as a means to conserve and extend the useful life of the potable water supply. The District completed a reclaimed water evaluation as required by the Revised Code of Washington (RCW) 90.46.112 and Washington Administrative Code (WAC) 173-240-050. King County Water District 125 overlays a significant portion of the District's service area. That District worked with King County in the development of the regional reclaimed water planning process and has committed to work with its customers and the county as appropriate to assess the feasibility of using reclaimed water for various non-potable water needs. Infiltration and Inflow The District participated in the King County Regional Infiltration and Inflow Control (I/I) Program. This program included flow monitoring through the District by drainage basins during the winter months of 2000 – 2002. Based on the flow and rainfall data collected for the ten largest rainfall events in the fall and winter of 2001 and 2002, the average calculated 30-minute peak I/I for the District was 3,789 gallons per acre per day (gpad). Valley View Sewer District was selected to participate in a pilot project with King County to test a new method of controlling I/I. The method implemented by the District was manhole rehabilitation, which consisted of rehabilitating manholes through chemical grouting or epoxy injection and adjusting frames and covers. However, there was no measurable I/I reduction observed due to these measures. SEPA The District completed a State Environmental Policy Act (SEPA) checklist for the Plan and, as lead agency, issued a determination of non-significance for the issuance of the Plan on January 24, 2012. There were no appeals. |
| A review of the specific statutes, rules, codes, and policies to the comprehensive sewer plan is as follows: |
|  | A. General and sewer plan-specific requirements of King County Code (KCC) 13.24.010 and 28.84. | Comments/findings |
| (1) | Review and approval by the King County Council is applicable to special purpose districts under Revised Code of Washington (RCW) 57.16.010(7); Review and approval by the King County Council is applicable to entities that provide sewer service in unincorporated King County (KCC 13.24) and Sewer districts that provide wastewater to the regional system under KCC 28.84. | The review and approval of the District 2011 Comprehensive Sewer System Plan (Plan) is required as the District is a special purpose district authorized by, and operated under, Title 57 RCW. The District’s service area lies within the cities of Tukwila, SeaTac, Seattle and Burien and unincorporated King County. A portion of the District’s wastewater flows to the regional treatment system with the remainder flowing to the Midway Sewer District or Southwest Suburban Sewer District. |
| (2) | The Plan shall be consistent with the King County Comprehensive Plan (KCCP) and development regulations and policies. | Yes. See below for details. For the KCCP, the applicable policies are listed along with the policy or operational activity the District takes related to the policy. |
| (3) | The Plan shall be adopted by that entity and approved by the King County Council as a prerequisite for the following: Operating in unincorporated King County; Approval of annexation proposals; Granting of new right-of-way franchises and right-of-way franchise renewals; and Approval of right-of-way construction permits, except for emergency permits issued under KCC 14.44.055. | The District's Board of Commissioners approved the Plan. The District’s service area includes a portion of unincorporated King County within the urban growth area (UGA). The District holds two franchises; franchise numbers 6426 and 8671 for sewer service that expire January 6, 2011, and June 1, 2017, respectively. The County will initiate a franchise update process with the District to address franchise 6426. |
| (4) | Plans should be submitted every six years or sooner if required by the Washington State Department of Ecology (DOE), or whenever sewer conditions have changed significantly within the sewer service area. | The District’s last wastewater plan was done in 2000. DOE’s approval of the Plan is pending. |
| (5) | Infrastructure for existing and future service areas based on adopted land use map. | Yes. |
| (6) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | The District has concluded that there is adequate capacity to accommodate peak flows and anticipated growth to the year 2030. |
| (7) | Consistent with Washington Administrative Code (WAC) 173-240-050. | Yes. |
| (8) | Discuss the following: Existing and planned flows, average and peak; Existing and planned flows for any basin discharging into the County system; Amounts of inflow and infiltration (I/I), in comparison with County standard of 1,100 gallons per-acre-per-day (gpad) and steps being taken to reduce; Areas of concern regarding corrosion and odor control, and steps being taken; and Opportunities for reclaimed water. | The existing and planned-for flows were developed with a standard method and are reasonable. The District discharges to the regional system and to the Midway Sewer District and Southwest Suburban Sewer District. Based on the flow and rainfall data collected for the ten largest rainfall events in the fall and winter of 2001 and 2002, the average calculated 30-minute peak I/I for the District was 3,789 gpad. I/I ranges from 1,100 gpad in some basins to nearly 13,200 gpad in sub-basin Val007. Valley View Sewer District was selected to participate in a pilot project with King County to test new methods of controlling I/I. The method implemented by the District was manhole rehabilitation, which consisted of rehabilitating manholes through chemical grouting or epoxy injection and adjusting frames and covers. However, there was no measurable I/I reduction observed due to these measures. There were no issues identified with either corrosion or odor control. The District completed an evaluation of reclaimed water use opportunities and worked with King County Water District 125 to monitor water use in the service area. |
|  | B. Public Sewer Service: 13.24.035 |  |
| (9) | All developments within UGA served by sewer unless on-site are allowed as temporary per KCC 13.24.136 and 13.08.070. | Yes, the District anticipates providing sewer service within its entire service area for new development in the unsewered areas and to sewer the remaining onsite systems. |
| (10) | Required elements of a sewerage general plan, as called for in RCW 36.94.010(3), are included in King County Comprehensive Plan and Technical Appendix. | The Plan has the general location and description of treatment and disposal facilities, trunk and interceptor sewers, pumping stations, monitoring and control facilities, channels, local service areas, and a general description of the collection system to serve the service area. The Plan also contains preliminary engineering detail to assure technical feasibility and discusses the methods of distributing the cost and expense of the system and the economic feasibility of plan implementation. |
|  | C. Consistency requirements: 13.24.060 |  |
| (11) | State and local health requirements. | The Plan will be reviewed by DOE. The Utilities Technical Review Committee (UTRC) review process included a representative of Public Health-Seattle & King County. |
| (12) | Elimination or prevention of duplicate facilities and a reduction of number of entities providing sewer service in King County. | The District has written agreements with local general purpose governments and other service providers as to areas to be served in order to coordinate service. |
| (13) | Promotion of most healthful and reliable services to the public. | Yes. |
| (14) | Provision of service at a reasonable cost, and maximization of use of public facilities. | Sewer rates appear reasonable. |
| (15) | Basin wide or multibasin water plans, sewerage plans, or both when approved by DOE or Washington State Department of Health. | The Plan makes no reference to the participation of the District with basin-wide or multibasin water plans, or sewerage plans. No regional water supply plan is applicable. The District is aware of, and supports, the planning done in the Green River basin for salmon recovery purposes. |
| (16) | Applicable state water quality, water conservation (e.g., RCW 90.48.495), and waste management standards. | The most significant water conservation efforts in the District’s service area occurred in the 1990’s. The water use by residents in the service area has remained relatively stable for the past decade. The District sees a very small impact on the sewer system from water conservation today. |
| (17) | Growth Management Act (GMA), chapter 36.70A RCW. | Yes, the Plan is consistent with the King County Comprehensive Plan and development regulations used to implement the GMA. The Plan uses population targets adopted by the cities under the GMA. |
| (18) | Ground Water Management Plans. | Ground water quality protection will be enhanced when the remaining onsite systems connect to the District. |
| (19) | Federally-approved habitat conservation plans and recovery plans under Endangered Species Act. | The District recognizes its responsibility to avoid ‘take’ of an endangered species in its operations. |
| (20) | Requirements for salmon recovery under RCW 77.85, and other plans, including regional water supply or water resource management plans. | The Plan makes no reference to the participation of the District with salmon recovery efforts within the watershed. No regional water supply plan is applicable. |
| (21) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | The District completed the reclaimed water evaluation called for in chapter 90.46 RCW and RCW 90.48.112. |
| (22) | State Environmental Policy Act documentation. | Determination of nonsignificance issued by the District on January 24, 2012, with no appeals. |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (23) | CA-5 and CA-6: adopt policies to protect quantity and quality of ground water. | Connection of houses and businesses with on-site septic to the District’s sewer system should reduce health risks from any failing septic systems. |
| (24) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users. | See number 21. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (25) | F-104: plan for provision of services to rural areas. | There are no rural areas within the District. |
| (26) | E-105: protect critical habitat. | Yes. The District plans to upgrade facilities and address possible I/I problems. This should reduce discharges and assist in improving the water quality of Puget Sound. |
| (27) | E-434: management and protection of water resources by King County through incentives, regulations, and programs. | The District does protect water resource quality through a well-run system. |
| (28) | E-466: protect ground water and develop strategies to compensate or mitigate for losses. | See above discussion regarding I/I and sewer service to properties which currently have no sewer service. |
| (29) | E-477: protect and enhance surface waters, including Puget Sound. | See number 26. |
| (30) | F-105: work with cities and service providers to provide services. | Yes, the District provides service within the cities of Burien, SeaTac, Seattle, and Tukwila. The County works with the District for that portion of the service area in unincorporated King County. |
| (31) | F-202: ensure adequate supply of public facilities to support communities. | Yes, the District used information from the most recent comprehensive plans of the jurisdictions it overlays. |
| (32) | F-203: work with cities, special purpose utilities, and other service providers to define regional and local services and determine appropriate providers. | Yes, the district has worked with King County to define the service area. The District has written agreements with local governments regarding service provision. |
| (33) | F-207: funding for growth should support facilities needed within UGAs, prioritized and coordinated through capital improvement programs (CIP), to comply with concurrency requirements. | Funding sources are identified to support identified needs, including facilities to serve anticipated population growth under local comprehensive plans. Within the next six years, the District plans to seek Public Works Trust Fund loans for four projects totaling just over $1.4 million dollars. All other projects will be funded by rates, general facility revenue from developers and proposed bonding. |
| (34) | F-208: support rural levels of development and not facilitate urbanization. | There are no rural areas within the District. |
| (35) | F-210: coordinate development of utility facilities. | Yes, the District has coordinated with neighboring jurisdictions to coordinate service. |
| (36) | F-212: King County’s CIP demonstrates that projected needs for facilities and services can be met within the UGA in compliance with concurrency requirements; where not possible, identify strategies including phasing and financing. | Yes. The District’s CIP identifies facilities and a funding strategy to ensure the District will meet anticipated demands. The District reviews its financial information each fall to ensure the CIP is in line with development in the service area. |
| (37) | F-213: water and sewer utilities that provide services to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and King County Comprehensive Plan. | Service in unincorporated King County is consistent with the KCCP. |
| (38) | F-215 and F-217: where an area wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | Not applicable as no deficiency was identified. |
| (39) | F-245: all development within UGA to be served by public sewers, with some exceptions. | Yes, the policy is being implemented. |
| (40) | F-246: King County and sewer utilities should jointly plan for phasing out of on-site systems within UGA. | Yes, the District anticipates its entire service area being served by sewers. |
| (41) | F-252: King County should monitor failing on-site systems and analyze options which may include connecting to sewerage systems where consistent with the King County Comprehensive Plan. | There is not a known significant number of failing on-site systems within the District’s service area. |