DOWL H K M	MEMORANDUM

DATE: April 1, 2009

TO: Steve Hirschey, Chair

King County Utilities Technical Review Committee

FROM: Toby Coenen, PE — DOWL HKM

Denise Stiffarm, K & L Gates LLP

Jed Reynolds, Lake Washington School District

SUBJECT: Wilder Elementary School — Sewer Extension

GENERAL OVERVIEW

This memo provides information regarding the Lake Washington School District's (the "District") request to extend sewer from the City of Redmond ("Redmond") to the existing Wilder Elementary School ("Wilder"). Wilder currently uses a holding tank and regular pumping (and transfer off-site) for waste disposal. The District is pursuing this alternative due to the expense and maintenance of the holding tank/pumping arrangement, as well as health and safety concerns.

Wilder is located at 22130 NE 133rd Street (King County Tax Parcel 212606-9015). Redmond's sewer service area boundary is one half mile to the east of the Wilder boundary. The Redmond sewer service area boundary also forms the boundary between the urban and rural area as designated by the King County Comprehensive Plan. Wilder is located on the rural side of the boundary.

Related to this proposal, Redmond has requested an amendment to Redmond's existing

sewer service area (via an amendment to the Redmond General Sewer Plan). Wilder currently sits within the Woodinville Water District (WWD) service area boundary. However, the nearest WWD sewer is nearly three miles away and WWD has no long-term plans to extend sewer to the vicinity. In contrast, Redmond's existing service area boundary and existing sewer infrastructure is less than one half mile east of the Wilder site. The goal of this effort is to permit the extension of sewer service from Redmond via a tightline to Wilder. (Redmond and VVWD will formally agree to the service arrangement through the execution of an Interlocal Agreement.)

PERMITTING REQUIREMENTS

In King County, sewer extensions are generally prohibited outside of the urban growth boundary to avoid encouraging urban levels of development. However, the King County Code ("KCC") and the King County Comprehensive Plan recognize that, under certain circumstances, extending sewer service to rural areas can serve the public's interest. KCC 13.24.134(A), as amended by ordinance 2008-0126, specifically allows sewer service in rural areas where such facilities are:

Ars.

DOWL HKM

8420 154th Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowlhkm.com

- Needed to address: (a) specific health and safety problems threatening the existing uses of structures; or (b) the needs of public systems with design daily average flows of more than three thousand five hundred gallons per day; and

- Tightlined; and

- A finding is made by the utilities technical review committee that no cost-effective alternative technologies are feasible and that an on-site sewer disposal system for the public school or public school facility would not protect basic public health, safety, and the environment during the use of this site for a school or school facility.

King County Comprehensive Plan Policy F-249 also provides, in part:

Public sewer expansions shall not occur in the Rural Area and on Natural Resource Lands except where needed to address specific health and safety problems threatening uses of structures or the needs of public schools. . . . Public sewers may be extended pursuant to this policy, only if they are tightlined and only after a finding is made by King County that no reasonable alternative technologies are technologically or economically feasible and that an on-site sewer disposal system for the public school . . . would not protect basic public health, safety, and the environment during the use of this site for a school[.]

Pursuant to the Code and Comprehensive Plan Policy, sewer service to the Wilder site is subject to the following findings:

- That the sewer extension is needed to address the needs of a public school with a design daily average flow of more than three thousand five hundred gallons per day;

- That the sewer extension will be tightlined;

- That no reasonable alternative technologies are technologically or economically feasible; and

- That an on-site sewer disposal system would not protect basic public health, safety, and the environment during the use of this site for a school.

These four points are addressed below.

DOWL HKM

8420 1541h Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowlhkm.com

THE SEWER EXTENSION IS NEEDED TO ADDRESS THE NEEDS OF A PUBLIC SCHOOL WITH A DESIGN DAILY
AVERAGE FLOW OF MORE THAN 3,500 GALLONS PER DAY:

Wilder Elementary School is a public school owned and operated by the Lake Washington School District No. 414.

KCC 13.24.134(A)(1), as amended, requires that a public school system have a design daily average flow of more than 3,500 gallons per day. Wilder's design daily flow is approximately 3,645 gallons of water per day. (CPL Engineering) 20011.)

THE SEWER EXTENSION WILL BE TIGHTLINED:

The applicable Code and Comprehensive Plan provisions state that rural sewer connections must be tightlined (run through an enclosed pipe free of future connection points). The intent of this requirement is to ensure that no future connections by adjacent property owners. The proposed sewer extension to the Wilder site meets this requirement. The new sewer pipe will be a two-inch force main conveying waste from a proposed school-owned pump station. Three elements of the pipe configuration will help prevent future connections:

- The pipe will be a continuous polyethylene pipe free of joints or other potential connection points;

- The pipe will operate under pressure; as such, it will not be possible to connect to the sewer without installing a pump; and

- Wilder's pump station will convey waste at rate equal to the two-inch pipe's capacity.

NO REASONABLE ALTERNATIVE TECHNOLOGIES ARE TECHNOLOGICALLY OR ECONOMICALLY FEASIBLE:

The District has three general alternatives to address Wilder sewage: (1) continue pumping; (2) construct an on-site sewage disposal or septic system; or (3) connect to the sanitary sewer. Each alternative, along with associated costs, are discussed below.

Please note that each alternative includes up-front capital costs and various annual costs such as maintenance. To provide a valid comparison, we determined the present value of any annual costs and totaled all expenses. This analysis is based on an assumed 20-year project lifecycle and a 6% discount and inflation rate. All costs are approximate and are intended to provide an order of magnitude comparison between alternatives. They do not represent precise construction or operating cost estimates. Also note that this comparison reviews just the costs of the alternative waste disposal strategies. We did not include other considerations such as long-term viability, chance of failure, or health and safety issues.

1.	The current method, rehabilitating the existing holding tank and continued pumping, is

economically impractical and unfeasible. Specifically, the District spends nearly

1 Coughlin Porter Lundeen Engineering Report, "Wastewater Disposal Holding Tank, Wilder Elementary LWSD No.414" (2001).

DOWL HKM

8420 154"' Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowlhkm.com

$11,000 each month on pumping, for an annual cost of close to $130,000. Based on current costs, over 20 years the total outlay would exceed $2,600,000 (not adjusted for inflation). Furthermore, the existing tank, like the previous tank that it replaced, shows continuing evidence of leaks. For continued use, this tank must be repaired to eliminate the leaks.

The expense of continued use of the existing tank (or a replacement tank) includes three general cost elements:

- Immediate repairs to correct the leaks,

- Ongoing pumping and regularly scheduled maintenance costs, and

- Periodic equipment replacement and upgrade costs.

| No. A | Item Description Temporary tank including connection to existing sewer, bypass piping, pump, controls and pump-out connection | Cost |  |
| --- | --- | --- | --- |
|  |  | Annual Cost N/A | Present Value $50000 |
| B | Pump, clean and refurbish tank. Recoat interior with epoxy resin. Re- plum connections and reinstall hardware. | N/A | $100,000 |
| C | Refurbish existing pump-out equipment | N/A | $10,000 |
| D | Reconfigure pump-out alarm and signal telemetry | N/A | $10,000 |
| E | Ongoing pumping costs | $130,000 | $2,600,000 |
| F | Annual maintenance for pump, controls and miscellaneous hardware | $1,500 | $17,200 |
| G | Periodic tank rehabilitation (assume a 10-year maintenance cycle) | N/A | $40,000 |
| H | Periodic pump replacement (assume a 10-year life cycle) | N/A | $25,000 |
| Total Present Value: |  |  | $2,802,250 |

Item G is determined based on incurring the replacement cost in year 10 of the 20-year life cycle, and Item H is determined based on replacement in years 5 and 15. In both cases, price inflation impacts the cost of the specific work but is offset by a corresponding return on investment of present dollars.

The most recent annual pumping and hauling costs (Item E) total nearly $130,000, a figure expected to increase by roughly 6% annually, or $7,800 per year. To simplify the calculations, we've assumed the cost increase is uniform over the 20 year life cycle rather than at an increasing rate typically associated with compounding inflation. However, please note that this greatly underestimates the true costs associated with annual pumping and hauling.

2.	The second alternative, constructing a conventional sewage disposal or septic system,

is technologically unfeasible. To consider the on-site septic system, the District retained a licensed septic designer to prepare a feasibility study evaluating the viability of an on- site septic system. (2008 Whalen Designs Study.) Note all conventional septic systems include three general elements: anaerobic treatment (septic tank); aerobic treatment

(native or imported soil media); and waste disposal (in-ground drainfield, typically

la

DOWL HKM

8420 154"' Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowihkm.com

Memorandum April 1, 2009 Page 5

integrated into the soil media). The July 21, 2008, study prepared by Whalen Designs concluded that the Wilder site "will not meet the minimum requirements sewage

disposal system for the existing elementary school." In other words, no soil on the Wilder site is capable of providing the third element: wastewater disposal. While soil can be imported to aid in aerobic treatment, neither the State nor King County allow supplementing the existing soil to achieve absorption rates adequate for waste disposal. Consequently, this alternative is not possible regardless of cost.

Despite being unfeasible, we understand the Utilities Technical Review Committee wants a cost of a school-sized septic system for the sake of comparing costs.

3.	As an alternative to the conventional septic system, the District has also considered a

A

Abandon existing holding tank and pump-out station

B

Reconfigure site plumbing to connect to new system

New septic system (tank, mound, pumps and piping)

D

Annual maintenance and monitoring

Cost

| Annual Cost | Present Value |
| --- | --- |
| N/A | $10,000 |
| N/A | $20,000 |
| N/A | $300,000 |
| $2,000 | 22,900 |
|  | $302,900 |

Total Present Value:

modified septic system. The disposal and typically the anaerobic treatment elements are similar to a conventional septic system, but alternative technologies are used to provide a higher level of aerobic treatment. These systems are increasingly required for large on-site systems or for facilities generating higher strength waste streams. The cost of alternative treatments varies significantly depending on the technology and the desired effluent quality. Alternative systems still rely on native soil drainfields for final waste disposal. Again, as demonstrated in the Whalen study, no soil on the Wilder site

is capable of providing wastewater disposal. As a result, this alternative is not possible for the same reason conventional systems are unfeasible.

Again, despite being unfeasible, the UTRC expressed an interest in understanding the relative costs of an alternative treatment technology.

| No. A | Item Description Abandon existing holding tank and pump-out station | Cost |  |
| --- | --- | --- | --- |
|  |  | Annual Cost N/A | Present Value $10,000 |
| B Reconfigure site plumbing to connect to new system |  | N/A | $20,000 |
| New septic system (tank, mound, pumps and piping) |  | N/A | $300,000 |
| D New alternative aerobic treatment system |  | N/A | $250,000 |
| MNAnnual maintenance and monitoring |  | $4,000 | 45,900 |
| Total Present Value: |  |  | $625,900 |

DOWL HKM

8420 1541h Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowlhkm.com

4.	The sewer alternative includes two primary construction elements: pump station and

force main (Items A through D). Additionally, connecting to the region's public sewer includes a one-time City of Redmond connection fee and King County capacity charge. Additional costs include:

- The City of Redmond's monthly sewer bill which covers the City's expense of operating their collection system; and

- King County's monthly bill to cover ongoing wastewater treatment costs. The overall monthly sewer bill is estimated at around $500 per month.

| No. A | Item Description Abandon existing holding tank and pump-out station |  | Cost |
| --- | --- | --- | --- |
|  |  | Annual Cost N/A | Present Value $10,000 |
| B | Reconfigure site plumbing to connect to new system | N/A | $20,000 |
| C | Pump Station & Controls | N/A | $100,000 |
| D | Force Main | N/A | $200,000 |
| E | Pump Station 0 & M | $2,500 | $28,800 |
| F | Periodic pump replacement (assume a 12-year life cycle) | N/A | $10,000 |
| G | City of Redmond annual maintenance cost of force main | $2,500 | $28,800 |
| H | City of Redmond one-time connection fee | N/A | $15,000 |
|  | City of Redmond & Metro annual cost of monthly sewer bill | $6,000 | $100,200 |
|  | King County Metro sewer Capacity Charge (15 years only) | $N/A | $43,700 |
| Total Present Value: |  |  | $556,500 |

Two of the four alternatives presented here are technically feasible: the holding tank and the sewer. The two on-site based strategies cannot be built because, regardless of how thoroughly the effluent is treated, there is no place to dispose of it on the Wilder site.

Of the two viable alternatives, the proposed sewer route is less than one-fifth of the cost of rehabilitating the existing tank and continuing to pump and truck waste. The expense of rehabilitating the existing tank and continued waste hauling, nearly $11,000 per month, renders the holding tank economically unfeasible.

AN ON-SITE SEWER DISPOSAL SYSTEM WOULD NOT PROTECT BASIC PUBLIC HEALTH, SAFETY, AND THE ENVIRONMENT DURING THE USE OF THIS SITE FOR A SCHOOL:

There is existing evidence of health and safety concerns related to the existing on-site sewer disposal system at Wilder. The current method of disposal at Wilder involves storing sewage in an underground tank before pumping it to a truck for transport and offsite disposal. This pumping occurs weekly --though often twice per week-- during the school year. In 2002, the District discovered that Wilder's original holding tank was leaking and immediately replaced it

DOWL HKM

8420 154th Avenue NE • Redmond, WA 98052 • Tel: (425) 869-2670 • Fax: (425) 869-2679 • www.dowlhkm.com

with the existing tank. Since that time, the District has discovered that the existing tank also leaks as evidenced by periodic fluctuations in the pumping volumes that coincide with heavy rainfall events. There is no certainty regarding why this location results in leaky tanks; however, the problem likely originates with unstable ground or highly expansive backfill causing the tank to crack. Ultimately, the fact that a tank installed explicitly to address the leak problem continues to be a concern indicates a new solution is warranted.

In addition, the tank pump-out process involves a risk clearly at odds with an elementary school: an accidental sewage spill would have far worse consequences at a school than at a residential, commercial or industrial facility. The current waste disposal strategy presents public health concerns that would be virtually eliminated by constructing a sewer.

CONCLUSION

The circumstances at Wilder support all four prongs of KCC 13.24.134(A) and the requirements of the King County Comprehensive Plan Policy F-249. The need for sewer service to Wilder Elementary School is clearly documented and will fully meet the intent of the relevant policies as adopted by the King County Council.

DOWL HKM