| Review of the City of Pacific 2008 Water System Plan |
| --- |
|  | A. General and water and sewer plan: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | Applicable to water utilities that distribute water within a Critical Water Supply Service Area in King County (Ch. 70.116 RCW) and that need to meet consistency requirements of RCW 43.20.260. | The City of Pacific (City) provides water service within the area covered by the South King County Coordinated Water System Plan (CWSP). The City’s 2008 Water System Plan (Plan) is subject to King County Council approval under Chapters 36.70A, 43.20 and 70.116 RCW. |
| (2) | Consistency with King County Comprehensive Plan and Development regulations, and policies including King County Code 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development. | The City’s Plan is consistent. |
| (3) | Infrastructure for existing and future service areas based on adopted land use map. | Yes, the City used adopted King County land use maps where appropriate. The Plan was reviewed by the King County Departments of Transportation and Development and Environmental Services (DDES). |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement. | The City’s Water Service Area (WSA) is within the planning area identified in the South King County CWSP. The WSA is smaller than the corporate boundaries of the City. The City is not averse to expansion of the WSA if circumstances recommend it. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | The City currently obtains its water from three wells located in a well-field. The projected maximum day demand in 2027 is approximately 1.87 million gallons per day (mgd) without conservation and 1.69 mgd with conservation, which will be met from the use of the wells. The City also has interties with the cities of Auburn, Algona, and Sumner. The two interties with the City of Auburn are for emergency use only. |
| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved CWSP. | The Plan is generally consistent with the South King County CWSP for the service area. The changes to the City’s WSA since the CWSP was adopted are within Pierce County, rather than King County. The Plan briefly notes the conservation program goals for the South King County CWSP and adds that those elements appropriate for the City were incorporated into its Plan. The City has maintained its existing program and added additional elements it deemed necessary and appropriate to meet its commitment to conserve water. The City is striving to achieve five percent water savings by 2012 and another five percent by 2027. The City is preparing to implement its current Water Use Efficiency Program, which will meet Washington State Department of Health (DOH) efficiency requirements under the Municipal Water Law. |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | State and local health requirements. | Yes. |
| (8) | Creation and maintenance of logical service areas. | Yes, the service area is logical. The City’s boundaries are fairly well fixed, although the Plan identifies a Potential Annexation Area abutting its westernmost boundary on the west plateau in King County. Extension of service to this area could require updating the City’s service area boundaries. |
| (9) | Elimination or prevention of duplicate facilities. | Yes. The City will not allow the operation of satellite water systems within its service area. The City has entered into agreements with neighboring water utilities about their respective service areas. |
| (10) | Promotion of most healthful and reliable services to the public. | Yes. A hydraulic analysis performed for the City shows that, with the addition of storage capacity or through use of interties, the City’s water distribution system has sufficient capacity to meet peak day and peak hour demand through the six- and 20-year planning periods. The City’s water rights are adequate to meet needs. The only problem is pumping volumes, which is where additional storage or interties may be needed. The hydraulic analysis of the City’s system identifies the need for improvements to the distribution system, particularly the replacement of undersized water mains in a recently annexed area to improve fire flow. Water purveyed by the City was evaluated for compliance with water quality standards and results indicate the City complies with the standards. |

| (11) | Provision of service at a reasonable cost, and maximization of use of public facilities. | The City’s rates for water service are comparable to the rates charged by similar utilities. The City is developing a graduated rate structure to encourage efficiency of water use during the summer months. |
| --- | --- | --- |
| (12) | King County Comprehensive Plan and other pertinent county adopted plans and policies. | Yes, there is consistency between the City’s Plan and the King County Comprehensive Plan. |
| (13) | Basin-wide or multibasin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (DOE) or DOH. | The City participated in the development of the South King County CWSP and the Plan is consistent with the CWSP. |
| (14) | Applicable state water quality, water conservation, and waste management standards. | The City tests the water produced from its wells and the water meets all water quality standards. The City’s water use per Equivalent Residential Unit (ERU) is 255 gallons per day (gpd), somewhat high for the region, but their peaking factor of two is lower than the regional average. The City’s conservation activities should reduce that number. The City’s distribution system loss of water is nine percent. The City recognizes it should improve on that percentage in the future. The City is projecting conservation savings of five percent by the year 2012, and another five percent by the year 2027, based on the 255 gpd per ERU from 2005-2006. |
| (15) | Water Resources Act (RCW 90.54). | The City’s conservation program is still in its initial stages, with the main part being the data collection element. The Plan outlines a number of recommendations that the City should begin to implement to enable it to comply with the Water Use Efficiency Rule adopted by DOH. The Plan makes no connection between the City’s conservation program and the requirements of RCWs 90.54.180 and 90.03.386. |

| (16) | Growth Management Act (GMA) (RCW 36.70A). | The City used population data from the Puget Sound Regional Council, as well as the City of Pacific Comprehensive Plan, in forecasting future water demand. For its planning, the City used a growth rate slightly greater than what it has experienced in recent years, based upon the actual increase in the number of service connections. The City’s Plan is sufficient to support the City in meeting adopted Growth Management household and employment targets. |
| --- | --- | --- |
| (17) | Ground water Management Plans. | There is a ground water management plan for South King County, but the City’s Plan makes no mention of it. The Plan discusses a Wellhead Protection Program for its wells developed in 1988 and updated by this Plan. Portions of the wellhead protection area, the five and ten year time-of–travel zones, overlap with unincorporated King County to the west of SR 167. |
| (18) | Federally approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | The City’s water comes in large part from wells located within the Puyallup-White River Watershed (WRIA 10). See 19 below. |
| (19) | Requirements for salmon recovery under RCW 77.85, and other plans, including regional water supply or water resource management plans. | The City has not been participating in the development of the WRIA 10 Management Plan but does not intend to act contrary to it. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | The City provides wastewater collection for its customers with treatment by the King County regional system. The City did not identify any sites that would be appropriate for the application of reclaimed water. The Plan did include the reclaimed water checklist provided by DOH as required by chapter 90.46 RCW. It does not appear the use of reclaimed water is feasible in the near term within the City. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |

| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | Not applicable. |
| --- | --- | --- |
| (22) | FW-12(c): ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Sufficient water supply for projected growth is available. There are no apparent linkages and little relevance of the Plan to fish habitat needs. |
| (23) | CA-5 and CA-6: adopt policies to protect quantity and quality of ground water. | The City is quite concerned about protection of its ground water resources and is using available resources and tools to protect ground water. See comment number 17 for information about the City’s wellhead protection program. |
| (24) | CO-5: water supply shall be regionally coordinated. | The City took part in the development of the South King County CWSP. The City also has intertie agreements with several of its neighboring communities. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The City is preparing to implement the water use efficiency program required by DOH. |
| (26) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users. | At present, there are not any sites in the City that would be suitable for the use of reclaimed water. See number 20 above. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (27) | E-434: management and protection of water resources by King County through incentives, regulations and programs. | Yes. |
| (28) | E-468: protect ground water, and develop strategies to compensate or mitigate for losses. | See comments 17 and 23. |
| (29) | E-477: protect and enhance surface waters, including Puget Sound. | Generally not applicable. Protection of Puget Sound and its tributary streams could possibly be enhanced by reduction of demand or using alternative sources of water, such as reclaimed water. |
| (30) | E-606: protect critical habitat. | Not applicable. |
| (31) | F-102: King County will provide or manage countywide services, which include wastewater, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands. | Yes, King County does provide wastewater treatment services for the City. |
| (32) | F-104: plan for provision of services to rural areas. | Yes, the City only provides water service to one rural area consistent with the King County Comprehensive Plan. The City has created a subarea for that part of the City that is within its Urban Growth Area (UGA) but that has not been annexed. That subarea process will determine how the City will ultimately approach the area. |
| (33) | F-105: King County work with cities and service providers to provide services. | The capital improvement program (CIP) is appropriately focused and adequate. |
| (34) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA. | Not applicable. The City’s supplies come from ground water sources. |
| (35) | F-202: ensure adequate supply of public facilities to support communities. | Yes, the City has sufficient water supplies and has arrangements for emergency supplies from adjacent communities. |
| (36) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | Yes, the City has agreements with all adjacent purveyors. |
| (37) | F-208: support rural levels of development and not facilitate urbanization. | Yes, see comment 32. |
| (38) | F-209: capital facility plans and improvement programs for services to unincorporated King County are consistent with the King County Comprehensive Plan. | Yes, the City’s CIP is consistent with the King County Comprehensive Plan. |
| (39) | F-210: King County helps coordinate development of utility facilities. | The City is willing to revise its CIP based upon input from citizens and to coordinate better with others, including King County. |
| (40) | F-212: King County CIP shall show that projected need for services and facilities in the UGA can be met in compliance w/concurrency requirements of the GMA. | The City’s CIP is intended to meet the needs of its entire service area, including both the urban and rural portions. |
| (41) | F-213: water and sewer utilities providing service to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and the King County Code. | For those parts of its service area that are rural, the Plan is reasonable and consistent with GMA and the King County Comprehensive Plan. |

| (42) | F-215: King County shall initiate a sub-area planning process with any service provider that declares, in capital facilities plan, an inability to meet service needs within service area. | Not applicable. The City did not identify any inability to meet service needs within its service area. |
| --- | --- | --- |
| (43) | F-217: where an area-wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | No area-wide water or sewerage deficiency identified. |
| (44) | F-225: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs. | The City has agreements with several of its neighboring communities for purchases of water on an emergency basis. The City does not participate in the distribution of water to other utilities. |
| (45) | F-226: Group A water systems must meet duty to serve requirement within service area as defined under CWSP or by individual water system plans. | See comments 4 and 5. |
| (46) | F-227-231: provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers. | The City recognizes its duty to serve within its service area and insists that all new water service be provided by the City. The City does not support Satellite Systems within its service area. |
| (47) | F-232: service from exempt wells limited to subdivisions with no more than six lots, and limited to one well unless an additional well is needed for flow requirements for the six lots; water from the exempt well is limited to no more than one-half acre irrigation. | The City requires that all new development connect to the City’s water system. The City does not support Satellite Systems within its service area. While the Plan acknowledges that there are some non-City sources within its service area, they are vestiges from the past. No new freestanding systems will be allowed to be created. |
| (48) | F-234-236: develop regional water supply plan with a role for reclaimed water as a source of supply. | See comment 20. |

| (49) | F-237: King County supports the use of interties consistent with planning, and implement approved ESA and Clean Water Act (CWA) response requirements. | The City has interties with neighboring communities to obtain some of its supply on an emergency basis. |
| --- | --- | --- |
| (50) | F-239: King County to partner with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | King County is willing to work with the City on these issues, particularly the provision of water service to adjacent unincorporated areas at an affordable price and the use and evaluation of reclaimed water opportunities. |
| (51) | F-240: Utilities Technical Review Committee (UTRC) to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for ground water, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | The UTRC did consider the given issues and recommends approval of the Plan. |
| (52) | F-241: in reviewing proposals for modified and expanded service area boundaries, the UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | The City can only expand to the west without having to reach agreements with adjacent purveyors. The Plan makes no mention of any desire on the part of the City to alter its service area boundaries at this time. |
| (53) | F-242: UTRC to develop a water accounting system, in conjunction with water utilities, to ensure the ability of utilities to issue certificates of availability. | The City uses letters of water availability to demonstrate water availability for DDES. |
| (54) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | Not applicable. The City’s storage facility is a tank. |
| (55) | F-244: ground water supplies should be protected by preventing land uses that may adversely affect quantity or quality. | See comments 5 and 17 for wellhead protection program comments. |