| Review of King County Water District No. 90 2006 Comprehensive Water System Plan |
| --- |
|  | A. General and water and sewer plan: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | Applicable to special purpose districts (Title 57 RCW) and water utilities distributing or obtaining water in unincorporated King County | The King County Water District No. 90’s (District) Comprehensive Plan (Plan) is subject to King County Council approval pursuant to RCW 57.16.010(6). The District obtains and distributes water in unincorporated King County, therefore, KCC 13.24 applies. |
| (2) | Consistency with King County Comprehensive Plan and Development regulations, and policies including King County code 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development | The District’s 2006 Plan is consistent except as noted. The District’s water franchise is number 13051 approved in March 1998 and expires in March 2023. |
| (3) | Infrastructure for existing and future service areas based on adopted land use map | Yes, the District used adopted land use maps. The Plan was reviewed by King County Department of Transportation (DOT) and the Department of Development and Environmental Services (DDES). |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement | The District proposes two changes to its service area, one in unincorporated King County, the other within the City of Renton. The District acknowledges that it has a duty to serve within its service area. The District did not demarcate a retail service area for water service. The District describes its water service area as generally co-extensive with the service area described in the East King County Coordinated Water System Plan (CWSP) except for areas on the southeast side and the proposed expansion in the northeast corner. The District appears to have the ability to serve the entire service area for the six and twenty-year periods covered by the Plan. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations | The District purchases water from the City of Seattle under a contract that expires in 2012, and is currently in negotiations with the City of Seattle for contract renewal. Assuming the contract is renewed, the District will be able to meet the projected water demand for the next six and twenty years. The projected maximum day demand in 2026 is approximately 5.71 million gallons per day (mgd) and total supply available is 4.97 mgd. The current contract water plus the self-supplied water appears insufficient to meet projected maximum day demand in 2026. |
| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved Coordinated Water System Plan (CWSP) | The Plan is inconsistent with the East King County CWSP for the service area. It appears several annexations in the past have expanded the District’s corporate boundary beyond that contemplated in the CWSP. The District also has pending, a plan to expand its corporate boundary in the northeast corner of the service area beyond the future service area as demarcated in the CWSP. In both cases, the expanded service area did not overlap with another utility’s claimed service area. When the CWSP is updated, the boundaries will have to be adjusted. The Plan does not reference the timely and reasonable dispute resolution process of the CWSP. The conservation program goals for the East King County CWSP set 1990 as the base year and established a 6.5 percent reduction in per capita water use as a conservation goal for the 1990 – 1995 period. The District met that goal. The CWSP conservation goal is outdated and should be revised or updated. |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | State and local health requirements | Yes. |
| (8) | Creation and maintenance of logical service areas | Yes, the service area is logical. Yes, a change to the service area boundaries is proposed. |
| (9) | Elimination or prevention of duplicate facilities | Yes. Pursuant to state law and King County Code, approval of new Group B systems by Seattle King County Public Health (SKCPH) will be conditioned with the requirement to be satellite owned or managed. The District is not an approved Satellite Management Agency (SMA); therefore, an approved Countywide contract SMA will be needed. The District has proposed but not implemented interties with neighboring water utilities. |
| (10) | Promotion of most healthful and reliable services to the public | Yes. A water system hydraulic analysis was completed and the District’s water distribution system has sufficient capacity through the six-year planning period to meet peak day and peak hour demand. A hydraulic analysis of the District’s system indicates area where fire flow does not meet current standards. These are generally areas developed prior to the Washington State Department of Health’s (DOH) most recent guidance on fire flows and include areas within the Urban Growth Boundary (UGB) in the eastern and southern portions of the District. Generally, the problem is attributed to undersized transmission lines. Where fire flow demands do not meet current standards, the capital improvement program (CIP) has targeted infrastructure improvements to address fire flow limitations. All new construction or rehabilitation of the system is required to meet existing fire flow standards. Outside the UGB for the residential sector, the fire flow standard of 500 gallons per minute for two-hour duration was met in the majority of the District. Upsizing of transmission mains will resolve identified problems. Outside the UGB the non-residential fire flow analysis indicated that fire flow needs were met. A storage analysis was conducted and the District identified where water storage requirements are not met. Operational changes are proposed to move several hundred service connections off pressure zones that are deficient in storage, to zones that have adequate storage, and that proposal is reasonable. Water purveyed by the District is evaluated for compliance with water quality standards and results indicate the District is compliant with the standards. |
| (11) | Provision of service at a reasonable cost, and maximization of use of public facilities | The District’s rates for water and sewer service are in the middle of the range of rate charges for similar utilities. The District has a rate structure to encourage efficiency of water use during the summer months. |
| (12) | King County Comprehensive Plan, and other pertinent county adopted plans and policies | Yes, there is consistency between the District’s Plan and the King County Comprehensive Plan, except as noted herein. |
| (13) | Basin wide or multibasin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (DOE) or Washington State Department of Health (DOH) | The District will participate in Seattle’s Regional 1% Water Conservation Program for the next two years. The District does not provide sewer services. All wastewater produced within the sewered portion of the District flows to the City of Renton and is then treated in the regional system. The Plan is consistent with the East King County CWSP, except as noted, and chapter 173-508 Washington Administrative Code (WAC), and the Cedar River – Lake Washington instream resources protection program. |
| (14) | Applicable state water quality, water conservation, and waste management standards | The District receives treated water from Seattle. The water withdrawn from the District’s well is treated for manganese and meets drinking water quality standards. The District’s water use as measured by what an average residential home uses is approximately 215 gallons per day (gpd). Historical data analysis of the average water use for a residential unit does not indicate if conservation activities are reducing water use. Lost and/or unaccounted for water has ranged from a high of 20 down to a low of 9 percent during the time-period since the last plan (1998). Replacement of nearly 30,000 lineal feet of old pipe water mains over the past years appears to have lowered the lost or unaccounted for water. The District participates in the regional conservation program. |
| (15) | Water Resources Act (RCW 90.54) | The District did not evaluate the conservation program from a cost effectiveness perspective. There is no connection of the conservation program to RCW 90.54.180 or RCW 90.03.386 requirements. The District’s Plan was drafted prior to the recently promulgated water use efficiency rule and does not acknowledge that a conservation goal will need to be established. However, Resolution No. 888 approved by the District in February 2008, indicates a commitment to continue to participate in Seattle’s regional conservation initiative. |
| (16) | Growth Management Act (GMA) (RCW 36.70A) | The District assessed population data from the Puget Sound Regional Council (PSRC) at the traffic analysis zone level to determine a future population base. The District felt the PSRC data under-estimated potential growth based, in part, on the historic growth rate within the District over the past six years. The District developed a customized population projection. The District appropriately used the land use zoning of King County for the unincorporated areas. |
| (17) | Groundwater Management Plans | There is a ground water management plan for East King County, and the District’s Plan makes no mention of that plan in relationship to its well. The District’s Plan does mention a wellhead protection program for its well and the District has much work to do to implement the program. |
| (18) | Federally-approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA) | The District’s primary source is a wholesale water contract from Seattle Public Utilities (SPU). SPU is implementing a habitat conservation plan for its Cedar River operations. The District’s water well is within the Cedar basin and the District acknowledges the hydraulic continuity between the well and the Cedar River. The District, in cooperation with the DOE, has developed a protocol for reducing ground water use when the Cedar River is below established instream flows. There is no discussion or evaluation of proposed water extraction from that well and potential affects, if any, to water bodies with listed fish. |
| (19) | Requirements for salmon recovery under RCW 77.85, and other plans, including regional water supply or water resource management plans | A salmon recovery plan under chapter 77.85 RCW was developed for the Cedar River basin. No reference to such planning is in the Plan. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW | A small portion of the District is overlaid by sewers. The District completed the reclaimed water checklist provided by DOH as required by chapter 90.46 RCW. One park with approximately 1 million gallons of water use per year was identified as a potential user of reclaimed water. It does not appear the use of reclaimed water is feasible in the near term within the District. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | Not applicable. |
| (22) | FW-12: ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Sufficient water supply for projected growth is available. No apparent linkages and little relevance of the water system plan to fish habitat needs. |
| (23) | CA-5 and CA-6: Adopt policies to protect quantity and quality of ground water. | The District participates in the East King County Ground Water Management plan implementation. For the wellhead protection program, see comment number 17. |
| (24) | CO-5: water supply shall be regionally coordinated. | The District is a contract buyer of Seattle wholesale water. The District coordinates with neighboring water and/or sewer districts. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The District implements the base conservation program required by the State. |
| (26) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users | One large water user was identified, a park, with a use of about 1 mgd. See number 20 above. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (27) | E-119: management and protection of water resources by King County through incentives, regulations and programs. | Yes. |
| (28) | E-123: protect and enhance surface waters, including Puget Sound. | Not applicable now. The potential for enhancing protection of Puget Sound may be realized if the District pursues use of reclaimed water to offset existing non-potable demand and/or uses reclaimed water for environmental enhancement. |
| (29) | E-155: protect groundwater, and develop strategies to compensate or mitigate for losses. | See comments 17 and 23. |
| (30) | E-204: protect critical habitat. | Not applicable. |
| (31) | F-102: King County will provide or manage countywide services, which include waste water, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands | Yes, for the unincorporated portions of the District’s service area. |
| (32) | F-104: plan for provision of services to rural areas. | Yes, the District provides water service in rural areas consistent with the King County Comprehensive Plan. The District recognizes that provision of sewer is only for those within the urban growth area. |
| (33) | F-105: King County work with cities and service providers to provide services. | The CIP program is appropriately focused. |
| (34) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA | Not applicable. |
| (35) | F-202: ensure adequate supply of public facilities to support communities. | Yes, although fire flow for certain areas is problematic. The CIP recognizes that and a program is in place to address fire flow needs. |
| (36) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | Yes. |
| (37) | F-207: support rural levels of development and not facilitate urbanization. | Yes, see comment 32. |
| (38) | F-208: capital facility plans and improvement programs for services to unincorporated King County are consistent with King County Comp Plan | Yes, the District’s CIP is consistent with the King County Comprehensive Plan. |
| (39) | F-209: King County helps coordinate development of utility facilities. | Yes with regard to wastewater services and less so with the water supply system. |
| (40) | F-211: King County capital improvement program shall show that projected need for services and facilities in the Urban Growth Area (UGA) can be met in compliance w/concurrency requirements of the GMA | The District serves both urban and areas zoned rural. The CIP seems reasonable. |
| (41) | F-212: water and sewer utilities providing service to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and the King County comp plan | The District serves both urban and areas zoned rural. The CIP is reasonable and consistent with GMA. |
| (42) | F-214: King County shall initiate a sub area planning process with any service provider that declares, in capital facilities plan, an inability to meet service needs w/in service area | Not applicable as the District did not identify any inability to meet service needs within the service area. |
| (43) | F-216: where an area wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | No area-wide water or sewerage deficiency identified. |
| (44) | F-224: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs | Not applicable as the District does not wholesale water. The District does coordinate with the City of Renton and Coal Creek Water & Sewer District. |
| (45) | F-225: Group A water systems must meet duty to serve requirement w/in service area as defined under CWSP or by individual water system plans | See comments 4 and 5. |
| (46) | F-226-230: Provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers | The District recognizes its duty to serve. The District has a few Group A and/or Group B public water systems in its service area and is planning to address their needs should that arise. |
| (47) | F-231: Service from exempt wells limited to subdivisions with no more than six lots, and limited to one well unless an additional well is needed for flow requirements for the six lots; water from the exempt well is limited to no more than one-half acre irrigation | Yes. |
| (48) | F-233-235: develop regional water supply plan with a role for reclaimed water as a source of supply. | See comment 20. |
| (49) | F-236: King County supports the use of interties consistent with planning, and implement approved ESA and Clean Water Act (CWA) response requirements | The District has interties with SPU for wholesale water. |
| (50) | F-239: King County partner with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | King County is willing to work with the District on these issues, particularly the provision of water service in unincorporated areas at an affordable price and the use and evaluation of reclaimed water opportunities. |
| (51) | F-240: UTRC to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for groundwater, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | The Utilities Technical Review Committee (UTRC) did consider the given issues and recommends approval of the Plan. |
| (52) | F-241: in reviewing proposals for modified and expanded service area boundaries, UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | The District is proposing to modify or expand service area boundaries in the northeast corner of the District. King County has pointed out in its comments to the District, the need for further clarification on “duty to serve” requirements. |
| (53) | F-242: UTRC to develop a water accounting system, in conjunction with water utilities, to ensure the ability of utilities to issue certificates of availability. | The District uses the water availability certificate document to demonstrate water availability for DDES. |
| (54) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | Not applicable. |
| (55) | F-244: groundwater supplies should be protected by preventing land uses that may adversely affect quantity or quality. | See comments 5 and 17 for wellhead protection program comments. |