The following descriptions apply to the status assigned to the recommendations:

| Status | Description |
| --- | --- |
| Complete | The recommendations have been implemented in full and there is no further action required. |
| In Progress | Implementation of the recommendations has begun but, due to complexity, resource availability, and/or budget constraints, the work is not yet completed. |
| Ongoing | Implementation of the recommendations has been completed and they are now systematically and/or programmatically subject to periodic review, updating, and/or continuous improvement. |
| Under Evaluation | Evaluation has begun to determine the feasibility of recommendations and their resource, prioritization, budgetary and scheduling constraints. |
| Implementing Alternative | Recommendations that were replaced with more effective, alternative solutions that meet the intent of the original recommendations. |
| Not Incorporated | After evaluation and consideration, the recommendations will not be implemented because they do not mitigate operation risks. |

| # | AECOM Table # | AECOM Recommendations | AECOM Comments | Status | Timeline | WTD Response |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Table 10 Plant Hydraulics | Evaluate ways to improve control strategies and flow management within the collection system. | Help delay peak flows to West Point. | Under evaluation | 2020 Initial Evaluation | WTD regularly considers collection system (pipeline) storage and control strategies when determining how to best manage flows. Storage is typically considered as an option when addressing collection system capacity constraints and is one of the control strategies to be evaluated in the Combined Sewer Overflow (CSO) planning work. |
| 2 | Table 10 Plant Hydraulics | Evaluate the collection system to identify new areas for storage. | For example, the Old Fort Lawton Tunnel. | Under evaluation | 2020 Initial Evaluation | WTD regularly considers collection system (pipeline) storage and control strategies when determining how to best manage flows. Storage is typically considered as an option when addressing collection system capacity constraints and is one of the control strategies to be evaluated in the CSO planning work. |
| 3 | Table 10 Plant Hydraulics | Add primary treatment technologies to the collection system. | Relieve West Point during high flows. | Under evaluation | 2020 Initial Evaluation | Adding treatment to the collection system has been and will continue to be considered as part of WTD's future long-term planning efforts. For example, WTD completed construction on the Georgetown Wet Weather Treatment Station in Q4 2022, adding primary treatment technology to the collection system. Where appropriate, projects with primary treatment technologies, will be submitted and considered as part of WTD's Six-Year Capital Improvement Plan. |
| 4 | Table 10 Plant Hydraulics | Consider implementing passive overflows at key locations. | Passive overflows that do not rely on equipment and controls provide the most failsafe mechanism to protect the plant and workforce. | Not incorporated | N/A | WTD has focused resources on eliminating flooding, overflows, and bypasses of the plant. This recommendation works against that effort as it may unnecessarily result in additional discharges to Puget Sound. WTD is proceeding with implementing the passive weir per recommendation 7, as it is a modification to provide redundancy for the plant’s existing bypass system. Additional passive overflow systems to facilities are not a favored approach given other planned system improvements underway and the potential for additional sediment and water quality impacts. |
| 5 | Table 10 Plant Hydraulics | Request that West Point Treatment Plant (West Point) be regulated as a combined sewer overflow outfall. | Currently able to discharge to outfalls at other locations. This would require coordination with Department of Ecology. | Not incorporated | N/A | WTD has focused resources on eliminating flooding, overflows, and bypasses of the plant. This recommendation works against that effort as it would result in additional discharges to Puget. Preliminary inquiries with Ecology indicate that re-designating the plant as a CSO location would not be supportable under current state regulations. Additionally, flow into the plant can be regulated at various CSO treatment locations, such as Elliott West, Alki, and Carkeek along with various CSO locations. |
| 6 | Table 10 Plant Hydraulics | Evaluate maximizing flow through the overflow weir by allowing head to build in the Influent Control Structure. | There is some freeboard above the weir, but flow is limited because of the elevation of the high-high level alarm, triggering the Emergency Bypass gate to open. Increasing the water level in the Influent Control Structure can negatively influence downstream (bar screens) and upstream (Ballard weir) systems. | Complete | Capital project started in 2019 | WTD completed a project that evaluated the viability and options to construct a passive weir. As a result, a project to construct the weir part of WTD's Six-Year Capital Improvement Plan. This project will need Ecology approval prior to implementation. |
| 7 | Table 11 Influent Control Structure | Evaluate adding a passive bypass weir. | Possibility of using the 84-inch Old Fort Lawton Tunnel to back flow to the Marine Outfall Gate at the Flow Diversion Structure. Utilize upstream storage, if any. | Complete | Capital project started in 2019 | WTD completed a project that evaluated the viability and options to construct a passive weir. As a result, a project to construct the weir is part of WTD's Six-Year Capital Improvement Plan. This project will need Ecology approval prior to implementation. |
| 8 | Table 11 Influent Control Structure | Avoid overriding controls of the Emergency Bypass gate to keep the gate manually closed. | None. | Complete | Implemented and ongoing | Standard operating procedures have been revised to ensure controls on the Emergency Bypass gate are not overridden except during maintenance. Implemented a new protocol designed to reduce non-emergency bypass events. Use of the new protocol prevented 3 non-emergency bypass events during the 2021 construction season. |
| 9 | Table 11 Influent Control Structure | Add automated Emergency Bypass gate control at the Influent Control Structure. | Consider adding a second solenoid alarm for redundancy and switching from hardwired interlock controls to control from the Ovation system. | Complete | Implemented | Equipment has been installed to allow for an emergency open of both the Emergency bypass and Emergency Marine Outflow gates. |
| 10 | Table 11 Influent Control Structure | Add ability to remotely operate Emergency Bypass gate from Main Control. | Provides rapid response without putting operators in harm’s way | Complete | Implemented | Operations staff now have the ability to open the Emergency Bypass gate remotely from the main control room. |
| 11 | Table 11 Influent Control Structure | Add ability to control influent gates from Main Control. | Clogged bar screens could cause water to back up in the Influent Control Structure and trigger the Emergency Bypass gate to open but would not close the influent gates. | Complete | Implemented | Operations staff now have the ability to control influent gates from Main Control. |
| 12 | Table 11 Influent Control Structure | Add control system programming that closes influent gates automatically when the Emergency Bypass gate is opened. | Clogged bar screens could cause water to back up in the Influent Control Structure and trigger the Emergency Bypass gate to open but would not close the influent gates. | Complete but under further evaluation | Implemented and ongoing. Complete Q2 2022. | Performance data collected through Q3 2021 showed some Flood Risk Reduction System (FRRS) vulnerabilities that will be addressed during the 2022 dry season. Working with a consultant for on-going system evaluation. Corrective actions may require engineering design prior to implementation. |
| 13 | Table 11 Influent Control Structure | Install flow meters on influent lines. |  | Not incorporated | N/A | WTD considered whether a flow meter would provide additional information to reduce operational risk and determined it would not reduce risk or improve overall plant control. West Point has a small footprint and relies on lift stations to pump wastewater through the treatment process. This means that West Point relies on level, not flow for overall plant control. |
| 14 | Table 11 Influent Control Structure | Add real-time collection system controls. | Incorporate historical collection system and watershed data into control strategies. | Complete | Ongoing | WTD considered this recommendation and confirmed that our offsite control system already incorporates real-time control of the collection system. As new collection system facilities come online, WTD will update our real-time control strategies. |
| 15 | Table 12 Preliminary Treatment | Continuously rake bar screen area during wet-weather events. | This is opposed to using a differential-level trigger. WTD has made this change. | Complete | Implemented and ongoing | West Point has updated its bar screen standard operating procedures to incorporate this recommendation. |
| 16 | Table 12 Preliminary Treatment | Raise the channel height at the bar screen area. | Provides surge protection and increased head in the Influent Control Structure for flow over the passive bypass weir. | Not incorporated (Implementing alternative) | Capital project started in 2019 | WTD completed a project that evaluated the viability and options to construct a passive weir. The evaluation showed that an upstream passive weir (see #6 & #7 above) would best prevent flooding without the need to raise the channel height. |
| 17 | Table 13 Raw Sewage Pump Station | Evaluate options to provide 440 mgd firm pumping capacity at raw sewage pumps. | Options and study items could include: 1. Adding a new pump. 2. Replacing existing pumps with new/larger capacity pumps. 3. Increasing the speed of the existing pumps. 4. Changing impellers to provide more flow. This may require a larger engine and modifications to the right-angle gearbox. 5. Controlling and limiting collection system flow to the plant at 330 mgd. 6. Considering providing more on-site and/or off-site CSO storage volume. | Complete | Capital project started in 2019 | WTD evaluated all recommendations related to the raw sewage pumps as one single evaluation, including options to increase the capacity of the raw sewage pumps. Changes to the collection system will be evaluated as part of the CSO planning work. A Raw Sewage Pump Improvement project is part of WTD's Six-Year Capital Improvement Plan. |
| 18 | Table 13 Raw Sewage Pump Station | Develop a detailed plan to operate at 330 mgd in preparation for losing a pump. | Not enough firm capacity at raw sewage pumps. | Complete | Implemented and ongoing | West Point Operations is implementing this recommendation as part of a larger Operator training improvement effort. That larger effort includes creating new, and modifying existing, training modules and standard operating procedures. |
| 19 | Table 13 Raw Sewage Pump Station | Install flow meters on influent lines. | Provides instantaneous influent flow for faster reaction times during high-flow events (compared to calculating influent flows from the effluent discharge). | Not incorporated | N/A | WTD considered whether a flow meter would provide additional information to reduce operational risk and determined it would not reduce risk or improve overall plant control. West Point has a small footprint and relies on lift stations to pump wastewater through the treatment process. This means that West Point relies on level, not flow for overall plant control. |
| 20 | Table 13 Raw Sewage Pump Station | Evaluate incorporating automatic controls through a supervisory control and data acquisition (SCADA) system. | Automatically stop pumps based on critical plant high-high water level set points to help prevent flooding. | Complete, but under further evaluation | Implemented and ongoing. Complete Q2 2022. | Performance data collected through Q3 2021 showed some FRRS vulnerabilities that will be addressed during the 2022 dry season. Working with a consultant for ongoing system evaluation. Corrective actions may require engineering design prior to implementation. |
| 21 | Table 13 Raw Sewage Pump Station | Provide additional staff training on operating raw sewage pumps. | During peak-flow events and various failure events, more training is needed. | Complete | Implemented and ongoing | West Point Operations is implementing this recommendation as part of a larger Operator training improvement effort. That larger effort includes creating new, and modifying existing, training modules and standard operating procedures as well as implementing an Operator Training Simulator. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 22 | Table 13 Raw Sewage Pump Station | Update safety procedures on operating the raw sewage pumps during peak-flow conditions. | Not enough firm capacity at raw sewage pumps. | Complete | Implemented and ongoing | See the response to #21 above. |
| 23 | Table 13 Raw Sewage Pump Station | Replace raw sewage pump engines with electric motors. Evaluate current condition of raw sewage pumps and determine expected life span. Provide backup systems to increase redundancy. Evaluate current condition and determine expected life span of the raw sewage pump station [piping system]. | Electric motors are more reliable and less expensive to maintain (high initial cost). Plan/budget for equipment maintenance, updates, and replacements. Redundancy reduces opportunity for failure. Estimate pressure capacity and incorporate corrosion inspections and durability to withstand earthquakes. | In progress | Implementation 2030 | A Raw Sewage Pump Improvement project began implementation in 2019 with commissioning planned for 2030. Alternatives Analysis is underway. The Department of Ecology has provided conceptual approval of the Pump Replacement project. WTD will forward the engineering report to Ecology for approval when complete. |
| 24 | Table 13 Raw Sewage Pump Station | Modify control strategy to include secondary instruments. | Redundancy reduces opportunities for failure. Automatically stop pumps based on critical plant high-high water level set points to help prevent flooding. | Complete, but under further evaluation | Implemented and ongoing. Complete Q2 2022. | Performance data collected through Q3 2021 showed some FRRS vulnerabilities that will be addressed during the 2022 dry season. Working with a consultant for on-going system evaluation. Corrective actions may require engineering design prior to implementation. |
| 25 | Table 14 Preaeration and Sedimentation Tanks | Replace level switches with modern tethered switches that do not require a stilling well and are less likely to fail. | WTD has already done this. | Complete | Implemented | Tethered switches were installed during the restoration work at West Point immediately following the February 9 flooding event. These floats have demonstrated greater reliability in industrial settings and can be tested without possibility of damage. |
| 26 | Table 14 Preaeration and Sedimentation Tanks | Modify control strategy to include secondary instruments. | Redundancy reduces opportunities for failure. | Complete, but under further evaluation | Implemented and ongoing. Complete Q2 2022. | Performance data collected through Q3 2021 showed some FRRS vulnerabilities that will be addressed during the 2022 dry season. Working with a consultant for ongoing system evaluation. Corrective actions may require engineering design prior to implementation. |
| 27 | Table 14 Preaeration and Sedimentation Tanks | Incorporate automatic controls through a supervisory control and data acquisition (SCADA) system. | Multilayered control system is not limited to a single interlock control. | Complete, but under further evaluation | Implemented and ongoing. Complete Q2 2022. | Performance data collected through Q3 2021 showed some FRRS vulnerabilities that will be addressed during the 2022 dry season. Working with a consultant for on-going system evaluation. Corrective actions may require engineering design prior to implementation. |
| 28 | Table 14 Preaeration and Sedimentation Tanks | Evaluate feasibility of a passive bypass. | Effluent can be diverted to the Emergency Bypass Outfall within the Flow Diversion Structure. | Not incorporated (Implementing alternative) | Capital project started in 2019 | This recommendation would provide roughly 30 million gallons of diversion, which would not provide significant relief. Diversion opportunities are being considered at head works as part of the passive weir project and through the development of West Point's life safety system. |
| 29 | Table 14 Preaeration and Sedimentation Tanks | Evaluate feasibility of connecting east and west primary effluent channels. | If one gate fails, near-full utilization of both primary sedimentation basins can continue. | Not incorporated | N/A | Connecting the primary effluent channels would allow primary effluent to flow over one or both gates. The failure of a gate would still result in a capacity reduction and loss of redundancy regardless of which gate failed. Alternatively, construction of a common channel is considered impractical given the existing plant design and site limitations. |
| 30 | Table 14 Preaeration and Sedimentation Tanks | Evaluate feasibility of a passive bypass. | Primary Effluent can be diverted to the Emergency Bypass Outfall and 3x3 vent within the Flow Diversion Structure. | Not incorporated (Implementing alternative) | Capital project started in 2019 | This recommendation would provide roughly 30 million gallons of diversion, which would not provide significant relief. Diversion opportunities are being considered at head works as part of the passive weir project and through the development of West Point's life safety system. |
| 31 | Table 14 Preaeration and Sedimentation Tanks | Reevaluate control strategy. | The control strategy can be based primarily on influent flow measurement, not a series of cascading system levels. | Not incorporated | N/A | WTD considered whether a flow meter would provide additional information to reduce operational risk and determined it would not reduce risk or improve overall plant control. West Point has a small footprint and relies on lift stations to pump wastewater through the treatment process. This means that West Point relies on level, not flow for overall plant control. |
| 32 | Table 15 Flow Diversion Structure | Evaluate feasibility of a passive bypass. | Options include creating a bypass from the Old Fort Lawton Tunnel or directing primary effluent to the Emergency Bypass Outfall pipe. | Complete | Capital project started in 2019 | WTD completed a project that evaluated the viability and options to construct a passive weir. A project began implementation as part of WTD's Six-Year Capital Improvement Plan. |
| 33 | Table 15 Flow Diversion Structure | Add automated Emergency Marine Outfall gate control at Flow Diversion Structure. | Previous practice was to manually override controls at low flow (<250 MGD). The Emergency Bypass gate is now always valved in. | Complete | Implemented and ongoing | Standard operating procedures have been revised to ensure controls on the Emergency Bypass (aka CSO Flow Diversion Gate) and the Emergency Marine Outfall. These gates cannot be overridden except during maintenance. |
| 34 | Table 15 Flow Diversion Structure | Add ability to remotely operate Emergency Marine Outfall gate at the Flow Diversion Structure from Main Control. | Provides rapid response without putting operators in harm's way. | Complete | Implemented | As part of the implementation of West Point’s life safety system a manual push button was installed in Main Control to allow remote, emergency opening of the Emergency Bypass and Emergency Marine Outfall gates. |
| 35 | Table 16 Effluent Pump Station | Provide a spare hydraulic unit that can operate with any pump control valve. | Redundancy reduces opportunity for failure. | Complete | Implemented | One spare hydraulic power unit was added to one series of effluent pump station pumps. A capital project installed a hydraulic power unit on the other series. This recommendation also addresses corrective action #1 required by Department of Ecology's Administrative Order. |
| 36 | Table 16 Effluent Pump Station | Provide redundant electrical power supply to all hydraulic power units. | Redundancy reduces opportunity for failure. | Complete | Implemented | Automatic transfer switches, to provide redundant power, were installed in mid-2017. This recommendation also addresses corrective action #1 required by Department of Ecology's Administrative Order. |
| 37 | Table 16 Effluent Pump Station | Add pressure relief valves at pump discharge lines. | Prevents pump from operating at zero flow/shut-off head conditions if control valve is closed while pump is operating. Discharge flow from pressure relief valves to gravity or pump discharge pipeline. | Not incorporated (Implementing alternative) | N/A | This recommendation is not being implemented because it does not address the root cause of the Effluent Pump Station failure nor improve reliability. As an alternative, West Point installed additional hydraulic power units to each Effluent Pump Station pump series. |
| 38 | Table 16 Effluent Pump Station | Provide portable ladder platform and hand wheel to manually operate the butterfly control valve. |  | Not incorporated (Implementing alternative) | N/A | This recommendation is not being implemented because a hand wheel would take 30-60 minutes to adjust the valves that need to be opened and closed in seconds for successful operation. As an alternative, WTD installed a secondary hydraulic power unit on a separate electrical power source to address the root cause of failure that resulted in this recommendation. |
| 39 | Table 16 Effluent Pump Station | Routinely examine data from vibration monitors to determine trends to help forecast pump maintenance and repairs. | None. | Complete | Implemented and ongoing | WTD procured a vibration monitoring vendor, purchased a mobile vibration monitoring system, trained maintenance staff on how to use the system, and implemented a vibration monitoring program. The vibration monitors and variable frequency drives have been replaced for all Effluent Pump Station pumps. |
| 40 | Table 16 Effluent Pump Station | Update vibration monitors. | None. | Complete | Implemented | All pump vibration monitors and variable frequency drives have been replaced. |
| 41 | Table 16 Effluent Pump Station | Evaluate the current condition of the Effluent Pumping System and determine its expected life span. | Plan/budget for spare parts and equipment maintenance, updates, and replacements. | Complete | Implemented and ongoing | WTD's current asset management practices accomplish this function by assessing, tracking and reporting condition and the end-of-life date for all West Point effluent pumping system equipment. |
| 42 | Table 16 Effluent Pump Station | Provide backup systems to increase redundancy. | Redundancy reduces opportunity for failure. | Complete | Implemented and ongoing | Redundancy is being added to critical Effluent Pump Station systems. Staff regularly evaluate current maintenance best practices and will adjust as needed to reduce the risk of equipment and system failures. |
| 43 | Table 16 Effluent Pump Station | Provide good maintenance, closely monitor systems, and stock critical spare parts. |  | Complete | Implemented and ongoing | WTD's current asset management practices require maintenance tracking and system monitoring. WTD's asset management and maintenance best practices accurately predict the critical parts, which WTD keeps in stock for the effluent pump station. |
| 44 | Table 16 Effluent Pump Station | Use a differential pressure sensor across the pump to estimate flow rate. | An algorithm would be developed that considers pump head/flow curve, pump speed, and pump differential pressure reading. The algorithm can be calibrated using information from the existing effluent flow meter. | Not incorporated | N/A | WTD considered whether developing and calibrating an algorithm would reduce risk or improve overall plant control. We determined this would not provide any additional information beyond what we already receive from the effluent flow meter and would not reduce operational risks. |
| 45 | Table 16 Effluent Pump Station | Provide controls that allow the Effluent Pump Station to operate at constant speed. | As a backup, provide controls that allow the pump to operate at constant speed while using the control valve to throttle discharge flow and maintain the wet-well water level set points. This would require adding single-speed starters. | Not incorporated | N/A | This recommendation is not being implemented as it is intended to allow the pumps to operate if the variable frequency drives fail but does not address the root cause of the failure or improve reliability. West Point has existing equipment redundancy to maintain treatment at full capacity in the event of a variable frequency drive failure. |
| 46 | Table 17 Electrical | Incorporate automatic transfer of switchgear main and tie breakers upon power loss. | Provides rapid response for substations that require faster response time than what personnel can provide. | Not incorporated | N/A | This recommendation is not being implemented because the plant's current, comprehensive procedure is required for safety reasons regardless of whether an automatic transfer system was in place. In addition, implementing this recommendation would be complicated, requiring additional structures at a site where space is limited. |
| 47 | Table 17 Electrical | Staff at least two electricians during high-flow events. | Two electricians are required for life-safety reasons. | Complete | Implemented and ongoing | WTD now requires instrumentation technicians, electricians, and mechanics on standby during weekday evenings and weekends to ensure sufficient coverage during high-flow events. |
| 48 | Table 17 Electrical | Provide additional permanently connected hydraulic power unit on the B side. | Include provisions for either unit to power all discharge valves. | Complete | Implemented | One spare hydraulic power unit was added to one series of Effluent Pump Station pumps. A capital project installed a hydraulic power unit on the other series. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 49 | Table 17 Electrical | Power Effluent Pump Station discharge valve controls from individual variable-frequency drives. | This is rather than powering from the hydraulic power units. | Not incorporated (Implementing alternative) | N/A | As an alternative to this recommendation, WTD improved reliability at the Effluent Pump Station by installing permanent hydraulic power units for each of the two sets of pumps, valves and variable frequency drives. |
| 50 | Table 17 Electrical | Analyze single points of failure for all components. | For example, a breaker that would feed control power to all Effluent Pump Station pump controllers or both primary and backup Ovation system controllers. | Complete | Implemented | During a recent interview, AECOM clarified this recommendation relates to the Ovation control system. AECOM considers this item fully addressed. |
| 51 | Table 17 Electrical | Add surge suppressors. | Medium-voltage transient surge suppressors on both sides of the main 15 kV switchgear. | Complete | Implemented | Medium Voltage transient surge suppressors are installed on both sides of the 15 kV switchgear. |
| 52 | Table 17 Electrical | Install power line monitors with transient waveform capture feature on each substation’s main breaker. | A maintenance tool to help analyze power system health and forensic analysis of failures. | Complete | Capital project started in 2019 | This project is part of WTD's Six-Year Capital Improvement Plan. |
| 53 | Table 17 Electrical | Conduct the remainder of testing related to the main switchgear 722-MSG01 circuit breaker ground fault 52-3 trip. | As soon as a plant shutdown is feasible. | Complete | Implemented | WTD completed the testing and changed the ground trip settings based on new, more accurate, modeling information. |
| 54 | Table 17 Electrical | Update standard operating procedure for Effluent Pump Station restart after ground fault. | Locally reset Effluent Pump Station vibration panels, variable-frequency drives, and pump local control panels upon a fault. | Complete | Implemented | West Point staff updated the standard operating procedures for the Effluent Pump Station. |
| 55 | Table 19 Instrumentation and Control | Add an “Interlock Active” indication light to the local control panels. | Alert the operators when the interlock is engaged (help with troubleshooting). | In progress | Implementation Q4 2024 | A project to install indication lights at the local control panels was delayed due to staffing vacancies that resulted in reallocation of resources to higher priority projects. Final connections to critical gate panels deferred to 2024 dry season to mitigate risk. |
| 56 | Table 19 Instrumentation and Control | Add a supervisory control and data acquisition (SCADA) system bypass switch to bypass the interlock. | This should be available only to the supervisors. | Not incorporated | N/A | The existing interlock is in place for safety reasons, and it is unsafe to bypass at any time during regular plant operations. The risk and consequence of another potential flooding event is being reduced by implementing other recommendations. |
| 57 | Table 19 Instrumentation and Control | Prevent interlock from being activated during high-plant-flow scenarios. | High-flow events pose a life-safety risk. | Not incorporated | N/A | See the response to #56 above. |
| 58 | Table 19 Instrumentation and Control | Remove the requirement to use both the High and high-high switches to activate the interlock. | Only the high-high switch would be required. | Not incorporated (Implementing alternative) | TBD | The recommendation results in a life safety system that relies on a single instrument. This increases the risk of false activation that can lead to inadvertent bypasses. WTD has been working with a consultant to develop an alternative solution that will be implemented to protect the plant from flooding due to high-level conditions and avoids reliance on single instrument activation. The solution will be a fully hardwired system with instrument redundancy. King County identified a solution to protect the plant from flooding due to high-level conditions and avoid reliance on single instrument activation. In Q4, a project Manager was identified, and initial planning discussions have begun. The timeline for completion will be approximately two years from design through implementation. |
| 59 | Table 19 Instrumentation and Control | Add an Ovation-level high-high signal to the hardwired interlock. | The Ovation signal should be set to activate before the float switches. | Not incorporated (Implementing alternative) | TBD | The recommendation adds interaction between the Ovation and independent hardwired interlock system. WTD best practice is to maintain separation of software and hardwired systems. WTD has been working with a consultant to develop an alternative solution that will be implemented to protect the plant from flooding due to high-level conditions and avoids reliance on single instrument activation. The solution will be a fully hardwired system with instrument redundancy. King County identified a solution to protect the plant from flooding due to high-level conditions and avoid reliance on single instrument activation. In Q4, a project Manager was identified, and initial planning discussions have begun. The timeline for completion will be approximately two years from design through implementation. |
| 60 | Table 19 Instrumentation and Control | Add remote start/stop pump controls to the Main Control room through the Ovation system. | Provides rapid response without putting operators in harm’s way. | Not incorporated (Implementing alternative) | N/A | The existing engines cannot be restarted remotely. Remote start will be considered as part of a future raw sewage pump replacement project. Remote stop capability has been implemented (see response to #61 below). |
| 61 | Table 19 Instrumentation and Control | Add a hard-wired emergency stop push button not controlled through Ovation. | Provides rapid response without putting operators in harm’s way. | Complete | Implemented | A manual push button has been installed in Main Control to allow remote, emergency stop of all four raw sewage pumps. |
| 62 | Table 19 Instrumentation and Control | Add remote start/stop pump controls to the Main Control room through the Ovation system. | Operations must send operators to the raw-sewage wet-well area to locally open/close the gates, taking time and potentially placing operators in harm’s way. | Not incorporated (Implementing alternative) | N/A | See the response to #60 above. |
| 63 | Table 19 Instrumentation and Control | Remove the requirement to use both the High and high-high switches to activate the interlock. | Only the high-high switch would be required. | Not incorporated (Implementing alternative) | TBD | See the response to #58 above. |
| 64 | Table 19 Instrumentation and Control | Add an Ovation-level high-high signal to the hardwired interlock. | The Ovation signal should be set to activate before the float switches. | Not incorporated (Implementing alternative) | TBD | See the response to #59 above. |
| 65 | Table 19 Instrumentation and Control | Add remote open/close gate controls to the Main Control room through the Ovation system. | Make these controls highly visible to respond in emergencies. | Not incorporated (Implementing alternative) | N/A | As part of the implementation of West Point’s life safety system a manual push button has been installed in Main Control to allow remote, emergency opening of the Emergency Bypass and Emergency Marine Outfall gates. Gates will not be allowed to close remotely. Operations staff is required to physically inspect equipment before gates are closed and equipment is restarted. |
| 66 | Table 19 Instrumentation and Control | Conduct an alarm management review workshop to properly prioritize alarms and remove or condition alarms. | The system is not optimized to prioritize alarms | Complete | Implemented and ongoing | WTD held an alarm management review workshop and implemented an alarm management improvement process. Plant staff reduced the number of nuisance alarms and will continue to review priorities and improve alarm procedures as part of ongoing operations and maintenance. This recommendation, in addition to #78 and #94, also address corrective action #2 required by Department of Ecology's Administrative Order. |
| 67 | Table 21 Staffing | Develop incentive programs to retain staff at West Point. | It is difficult to retain employees at West Point. | Complete | Implemented and ongoing | Attempts to negotiate incentive pay for new employees at West Point through the 925 bargaining process was unsuccessful in Fall 2017. WTD provided more detail on its ongoing staff retention efforts as part of this West Point Quarterly Report transmitted to the Council in February 2018. |
| 68 | Table 21 Staffing | Extend aspects of the Operator-in-Training program to existing staff. | Currently the Operator-in-Training Program is only for new hires with no previous wastewater treatment plant experience. | Complete | Implemented and ongoing | WTD reviewed and updated its standard operating procedures. Operations staff now have 1-on-1 training and more formal communications between crews. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 69 | Table 22 Operators | Create an Emergency Bypass standard operating procedure. | If a standardized process is in place, the operators could operate the plant as it is designed. | Complete | Implemented and ongoing | WTD implemented standard operating procedures on use of the Emergency Bypass gate. These procedures will continue to be improved as part of a larger Operator training improvement effort. Also, see response to #21. |
| 70 | Table 22 Operators | Change the “no bypass” philosophy. | This is important to protect life safety and equipment and to reduce the amount of time the plant is in bypass mode. | Complete | Implemented and ongoing | WTD management has clearly communicated that the Emergency Bypass gate is a tool to be used as required. Operations also instituted new guidelines regarding the appropriate use of the Emergency Bypass gate. Operators are being trained using desktop exercises and scenario-based discussions to train on emergency response procedures. These exercises will be part of the new simulator training referred to in recommendation #92. |
| 71 | Table 22 Operators |  | Important to keep the environmental protection mission of the organization. | Complete | Implemented and ongoing | See response to #70 above. |
| 72 | Table 22 Operators | Add an Emergency Bypass override button at the Main Control room. | Currently this is embedded in the control strategy. | Complete | Implemented | WTD installed equipment in Main Control to allow remote, emergency opening of the Emergency Bypass and Emergency Marine Outfall gates. |
| 73 | Table 22 Operators | Provide hands-on Emergency Response Plan training. | None. | Complete | Implemented and ongoing | Emergency Response training sessions have been increased from one per year to two. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 74 | Table 22 Operators | Run the hydraulic simulation model so operators know narrow time margins and potential consequences. | None. | Complete | Implemented and ongoing | WTD developed and deployed a computer model (simulator). This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 75 | Table 22 Operators | Implement a Life Safety Management system. | An aspect of this type of process is that it focuses on the process rather than the individual worker to avoid scapegoating and to effectively reduce risk. | Complete | Implemented and ongoing | WTD hired a Life Safety Coordinator who completed an initial Life Safety Evaluation. That evaluation, which will be continuously refined, provides a framework of recommendations that the West Point employees will implement and maintain. |
| 76 | Table 22 Operators | Add an automated call program to contact on-call personnel. | None. | Not incorporated (Implementing alternative) | N/A | As an alternative, WTD implemented a two-way communication protocol that is required to confirm contact between personnel. A secondary operator is responsible for making calls while the lead operator manages control of the plant. |
| 77 | Table 22 Operators | Increase the number of staff on duty in Main Control during wet-weather events. | None. | Complete | Implemented and ongoing | When weather predictions indicate heavy rainfall, the minimum amount of emergency/wet weather staffing has been increased to comply with new high flow protocols and procedures. |
| 78 | Table 22 Operators | Conduct an alarm management review workshop to properly prioritize alarms and remove or condition alarms. | The system is not optimized to prioritize alarms. | Complete | Implemented and ongoing | WTD held an alarm management review workshop and implemented an alarm management improvement process. Plant staff reduced the number of nuisance alarms and will continue to review priorities and improve alarm procedures as part of ongoing operations and maintenance. This recommendation, in addition to #66 and #94, also address corrective action #2 required by Department of Ecology's Administrative Order. |
| 79 | Table 22 Operators | Add a visual beacon/strobe-type alarm in the control room. | To warn the operators in the control room that flooding was imminent unless action is taken. | Complete | Implemented | Completed during installation of the FRRS system. A light and audible alarm were installed in the control room to warn operators of potential flooding conditions. |
| 80 | Table 22 Operators | Provide Emergency Communications training. | Should be part of Emergency Response Plan training. | Complete | Implemented and ongoing | Operations staff have been trained and Emergency Communications training has been incorporated into the West Point Emergency Response Plan. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 81 | Table 22 Operators | Practice standard operating procedures for Effluent Pump Station restart. | This was listed as a step to be checked on the standard operating procedure for Effluent Pump Station restart. Recent issues with EPS pumps have been related to vibration, and based on this previous experience, the operators did not expect power to the valves to be an issue. | Complete | Implemented and ongoing | WTD updated its standard operating procedures and Operations staff have been trained using those updated materials. |
| 82 | Table 25 Training | Create a designated emergency evacuation path. | Train often on designated emergency evacuation path. | Complete | Implemented and ongoing | A designated emergency evacuation path exists, and this has been reinforced and emphasized in the Emergency Response Plan. |
| 83 | Table 25 Training | Develop standard operating procedure for tunnel entry. | Develop a standard operating procedure for tunnel entry, particularly to avoid entering at high flows. | Complete | Implemented and ongoing | Immediately following the flood event, WTD implemented standard operating procedures to limit, and closely monitor, tunnel entry by employees during periods of high flows. |
| 84 | Table 25 Training | Review operator training program. | Need to assess the appropriateness and amount of training provided. | Complete | Implemented and ongoing | West Point implemented weekly training with a technical trainer and updated training materials. In addition, Operation staff conduct daily training and lessons learned sessions within and between crews. This recommendation also addresses corrective action #5 required by Department of Ecology's Administrative Order. |
| 85 | Table 25 Training | Increase number of operators on duty. | Operators need time on nonemergency shifts to gain on-the-job training across the plant. | Complete | Implemented and ongoing | Operations vacancies have been filled. WTD also expanded its existing training program to improve the number and quality of candidates for future vacancies. This was done by hiring 15 additional operator-in-training and term-limited temporary (TLT) staff who will be trained and competitive for hire into career service positions. Additionally, West Point updated standard operating procedures and increased the type and frequency of operator training. West Point employees continue to evaluate how to improve all training, especially emergency response, and will implement training improvements as they are developed. |
| 86 | Table 25 Training | Provide hands-on Emergency Response Plan training. |  | Complete | Implemented and ongoing | Emergency Response training sessions have been increased from one per year to two. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 87 | Table 26 Equipment and Systems Testing | Add waterproof lighting in the basement. |  | Not incorporated (Implementing alternative) | N/A | As an alternative to this recommendation, WTD implemented revised standard operating procedures that limit and monitor tunnel entry during periods of high flow. |
| 88 | Table 26 Equipment and Systems Testing | Have two permanent skids hooked up at all times. | Have online but connected. | Complete | Implemented | One spare hydraulic power unit was added to one series of Effluent Pump Station pumps. A capital project replaced the temporary installation for the one on the other series of pumps. This recommendation also addresses corrective action #1 required by Department of Ecology's Administrative Order. |
| 89 | Table 26 Equipment and Systems Testing | Secure walkway covers. | Fixed. | Complete | Implemented | Walkway covers have been bolted down. |
| 90 | Table 26 Equipment and Systems Testing | Revise standard operating procedure for annual plant hydraulic safety. | It was done this way because of multiple tank leaks experienced when water levels are above normal. This has been fixed. | Complete | Implemented and ongoing | A review and update of standard operating procedures has been completed and float testing is scheduled for twice a year. |
| 91 | Table 26 Equipment and Systems Testing | Implement a Life Safety Management system. | A Life Safety Management system should be developed and implemented to reduce risks and improve safety for the staff at the plant, protect the equipment, and reduce the duration of bypass events. | Complete | Implemented and ongoing | A Life Safety Coordinator has been hired and an initial Life Safety Evaluation was completed. That evaluation, which will be continuously refined, provides a framework of recommendations that the West Point employees will implement and maintain. WTD and King County IT are working on a joint Enterprise Asset Management System (EAMS) that will integrate with LSM functions. Until the EAMS is in place, WTD implemented an LSM SharePoint site and chain of custody routing forms. |
| 92 | Table 26 Equipment and Systems Testing | Develop a dynamic computer model to simulate plant hydraulic conditions. |  | Complete | Implemented and ongoing | A computer model (simulator) has been developed and deployed. This recommendation also addresses corrective action #4 required by Department of Ecology's Administrative Order. |
| 93 | Table 26 Equipment and Systems Testing | Implement routine testing of the Primary Effluent gate interlock indicator in Area Control Center 1. |  | Complete | Implemented and ongoing | West Point Maintenance employees will conduct an interlock test as part of their annual float testing procedure. |
| 94 | Table 26 Equipment and Systems Testing | Conduct an alarm management review workshop to properly prioritize alarms and remove or condition alarms. | Alarm criticality ratings should be reviewed. Only life-safety/hydraulic protection–related alarms should be classified as criticality level 1. These alarms should remain visible until cleared. | Complete | Implemented | WTD has completed an initial alarm management workshop on all Priority 1, 2 and 3 alarms. In addition, WTD has established a WP Alarm Steering Committee that meets regularly with stakeholders to further identify nuisance alarms and refine alarm priority levels. Alarms are now being compiled and tracked on a dashboard to provide tracking and visibility of overall frequency levels and to identify alarms that do not meet standards. A second alarm management workshop was completed in February 2021. to further eliminate potential alarm flood conditions and apply strategic measures to mitigate nuisance behaviors. This recommendation, in addition to #66 and #78 also address corrective action #2 required by Department of Ecology's Administrative Order. |
| 95 | Table 26 Equipment and Systems Testing | Revise standard operating procedure for Effluent Pump Station reset. | Need to specify the amount of time operators have during different flow conditions. Standard operating procedure specifies 2 attempts for restart. | Complete | Implemented and ongoing | WTD implemented a standard operating procedure for the Effluent Pump Station that specifies two restart attempts and updated training also emphasizes that procedure. |
| 96 | Table 27 Maintenance Procedures | Implement a Life Safety Management approach to all maintenance not included in Process Safety Management. | Implement a Life Safety Management approach to all maintenance not included in Process Safety Management. | Complete | Implemented and ongoing | WTD hired a Life Safety Coordinator who completed an initial Life Safety Evaluation. That evaluation, which will be continuously refined, provides a framework of recommendations that the West Point employees will implement and maintain. |
| 97 | Table 27 Maintenance Procedures |  | Maintenance may negatively affect component performance if the execution is incorrect, insufficient, delayed, or excessive. | Complete | Implemented and ongoing | WTD hired a Life Safety Coordinator who completed an initial Life Safety Evaluation. That evaluation, which will be continuously refined, provides a framework of recommendations that the West Point employees will implement and maintain. |
| 98 | Table 27 Maintenance Procedures |  | Organized communication is a component of a Life Safety Management system. | Complete | Implemented and ongoing | WTD hired a Life Safety Coordinator who completed an initial Life Safety Evaluation. That evaluation, which will be continuously refined, provides a framework of recommendations that the West Point employees will implement and maintain. |