Road Right-of-Way Drainage Trunk Line Inventory

Prepared in accordance with 
Ordinance 17941, Section 77, as amended by Ordinance 18110, Section 30, Proviso P3

August 2016

# Department of Natural Resources and Parks

# Water and Land Resources Division

# and

# Department of Transportation

# Road Services Division

#### Table of Contents

Introduction	3

Executive Summary	3

Report Requirements	4

- The location and condition of the drainage trunk system within	4
major road rights-of-way in unincorporated King County

- The estimated accuracy of the resultant database	6

- An analysis of the data to assess risks of failure and failure	6
impacts

- A prioritized program for maintenance, including replacement	7 schedule and costs

Introduction

Ordinance 17941, Section 77, as amended by Ordinance 18110, Section 30, Proviso P3 requires the King County Executive to transmit a report to the Council that inventories and assesses the drainage trunk line within major road rights-of-way in unincorporated King County.

Specifically, the Ordinance requires the report to include:

- The location and condition of the drainage trunk system within major road rights-of-way in unincorporated King County;

- The estimated accuracy of the resultant database;

- An analysis of the data to assess risks of failure and failure impacts; and

- A prioritized program for maintenance, including replacement schedule and costs.

This report addresses each requirement under a separate heading that corresponds to the particular requirement.

Executive Summary

The Water and Land Resources (WLR) Division of the Department of Natural Resources and Parks and the Road Services Division (Roads) of the Department of Transportation collaborated on the development of this report. The two agencies hired HDR, Inc. as the prime consultant to conduct an inventory and business risk assessment of the drainage trunk system within major road rights-of-way.

Much of the County’s road drainage system is at or nearing the end of its useful life. Since the largest and most costly components of this aging network are the pipe systems and metal culverts 24 inches or larger in diameter, that is where the consultant focused the inventory and assessment. Below are key findings from the consultant.

- There are just under 6,000 drainage assets >24” in the road rights-of-way in unincorporated King County.

- About 4 percent of these drainage assets are projected to be in critically poor condition, at imminent threat of failure.

- For the next 10 years, costs of ownership range from $335 million to $500 million, depending on level of service provided.

- The lowest level of service evaluated ($335 million over 10 years) assumes that all failing assets are replaced as they fail. If this level of service is not funded, then the response to failing assets will be less replacement and more road or lane closures or posting of warning signs to manage and minimize risk within available budget.

For the approximately 900 assets (15 percent) that have been mapped and inspected, the consultant identified $25.7 million in on-going and one-time actions over the next 10 years to mitigate risk. This includes $6.5 million in immediate preservation actions for 33 mapped and inspected assets verified to be at critical risk.

The results of this study are being used to inform the analysis for the development of the surface water management fee and the 2017/2018 budget proposals for the two participating agencies, WLR and Roads. The consultant’s report can be found online at http://your.kingcounty.gov/dnrp/library/water-and-land/stormwater/KC_ROW_Drainge_Assessment_Final_Report.pdf.

Report Requirements

The location and condition of the drainage trunk system within major road rights-of-way in unincorporated King County

Historically when road drainage systems were built, they were not necessarily mapped or recorded. This meant WLR and Roads could not assume the existing inventory was complete. In addition, the condition of the drainage assets that were mapped was not assessed and updated on a regular basis. To undertake the analysis for this report, WLR and Roads directed the consultant to develop different data sets according to three criteria – whether the assets were known, whether they were mapped, and whether their condition was verified by onsite inspection.

The analysis is built on the following data sets of assets:

- Mapped and inspected to verify condition: Age and material suggested these assets could be of concern, so the consultant inspected them to verify condition (897 assets);

- Mapped, condition not verified: These assets were not inspected because either they were inaccessible (123 assets) or age and material suggested they were not of concern in the near term (3,315 assets); for purposes of analysis, the asset conditions were presumed based on age and material rather than inspection;

- Unknown so not mapped and not inspected: Actual location and condition of these assets were not known but were extrapolated using a Geographic Information System (GIS) model that looked at areas of similar zoning and ratios of drainage assets to roadway length (extrapolation model projected approximately 1,627 assets).

To locate and assess drainage assets within major road rights-of-way, the consultant divided the Unincorporated County into 14 areas as shown in Figure 1. Assets in each data set and area were rated critical, high, medium, and low for risk exposure according to the verified, presumed, or extrapolated condition assessment. Critical assets were those considered at imminent threat of failure.

Table 1 shows for each data set the quantity of assets, percent of total drainage assets, number and percent of assets rated critical, and the confidence level in the condition ratings. The condition rating used to determine the confidence level considers the probability of the asset failing.

Figure 1. Map areas used to locate drainage assets in major road rights-of-way.

Table 1. Summary of assets by data set.

| Data Set | # of Assets in Data Set | % of Total Assets | # of Critical Assets | % of Critical Assets in Data Set | Confidence Level in Condition Rating |
| --- | --- | --- | --- | --- | --- |
| Mapped assets, inspected to verify condition | 897 | ~15% | 33 | ~3.7% | 71% |
| Mapped assets, not inspected, condition not verified | 3,438 | ~58% | 104 | ~3% | 37% |
| Unknown and unmapped assets, condition not known | 1,627 | ~27% | 102 | ~6% | 6% |
| TOTAL: | 5,962 | 100% | 239 | ~4% |  |

The estimated accuracy of resultant database

The estimated accuracy of the database can be measured by the confidence level in the condition ratings for the drainage assets. As shown in Table 1, the confidence level in the condition ratings for the mapped assets that were not inspected by the consultant is roughly half (37 percent) that of those assets the consultant did inspect (71 percent). The confidence level in the condition rating for the extrapolated assets that have not been mapped or inspected is very low (6 percent). This makes sense because field verifying an asset’s condition provides greater accuracy than extrapolating an asset’s existence, location, and condition through assumptions and GIS projections.

An analysis of the data to assess risks of failure and failure impacts

To assess risks of failure and failure impacts in both the near term and the long term, the consultant projected costs of ownership and business risk exposure for four different levels of service over 10 years and 100 years, using all three data sets of drainage assets > 24” in the major road rights-of-way in unincorporated King County. The consultant found the highest level of service costs the most to manage in the 10-year timeframe but has the lowest business risk exposure and costs the least over the 100-year timeframe; under this scenario, assets are rehabilitated or replaced before they are expected to fail, which increases the near-term management costs but decreases the long-term costs associated with potential asset collapse, such as for property damage, impacts to adjacent landowners, and possible road closures.

Table 2 below presents the costs of ownership and business risk exposure by levels of service. The table defines each level of service and its respective backlog of uncompleted actions, provides ownership costs over the next 100 years and the next 10 years, and states the 100-year maximum business risk exposure. The business risk exposure runs on a scale of 0 to 100, where 0 is the lowest risk exposure and 100 is the highest.

As Table 2 shows, over 10 years, the lowest level of service (D) costs less than the highest level of service (A); on the other hand, D has a very high maximum risk exposure (81 out of 100). In addition, level of service A costs less over the 100-year timeframe than level of service D when computed in net present value. Level of service B is not included in Table 2 because assumptions upon which it was built treated the backlog of actions inconsistently from the other levels of service, resulting in skewed preservation costs that could not be fairly compared to those of the other levels of service.

Table 2. Costs of ownership by levels of service.

| ID | Level of Service | Backlog | Ownership Costs over Next 100 Years, in Net Present Value | 100-Year Maximum Business Risk Exposure | Ownership Costs over Next 10 Years, in Real Costs |
| --- | --- | --- | --- | --- | --- |
| A | Manage all assets to lowest risk tolerance | Eliminated in first year, none created in future | $750 M | 58 | $500 M |
| C | Manage critical risk assets | Slowly eliminated, more added over time | $815 M | 66 | $348 M |
| D | Run assets to failure, respond to emergencies | Grows over time | $829 M | 81 | $335 M |

A prioritized program for maintenance, including replacement schedule and costs

In addition to projecting costs and risk levels for both the mapped and extrapolated drainage assets in the major road rights-of-way, the consultant also looked at immediate risk mitigation actions for assets known to be in critical condition. To recommend immediate actions for the mapped assets where the condition was verified through inspection, the consultant estimated costs for one-time preservation actions and ongoing operations. To reduce the likelihood of failures, the focus is on replacing assets in the most critical condition, monitoring assets nearing critical condition, conducting essential maintenance, and expanding what is known about the inventory and condition of the remaining assets.

The recommendations are shown in Table 3 and include only the 897 mapped and inspected assets. Not included are the mapped assets where the condition has not yet been verified and the unknown assets that are unmapped and condition unknown. Exhibit A summarizes mapped and inspected assets by verified condition and recommended mitigation action for each map area.

Table 3. Cost estimate for near-term risk mitigation actions for mapped and inspected assets.

| Action | Cost Estimate | Cost Basis |
| --- | --- | --- |
| On-going mapping, inventory, and condition assessment | $2,000,000 | 10-year cost |
| Enhanced condition assessment a | $900,000 | 10-year cost |
| Routine inspection b | $140,000 | 10-year cost |
| Triggered inspection c | $60,000 | 10-year cost |
| Maintenance cleaning d | $340,000 | 10-year cost |
| Maintenance repair e | $1,720,000 | 10-year cost |
| Preservation rehabilitation f | $700,000 | one-time cost |
| Preservation replacement g | $19,880,000 | one-time cost |
| Total Cost | $25,740,000 |  |

Assumptions used to build the prioritized maintenance program in Table 3:

a.	Enhanced condition assessment for 140 assets every 2 years, 116 assets every 5 years,
and 242 assets every 10 years; assigned based on calculated business risk exposure scores.

b.	Routine inspection of 25% of assets each year.

c.	Triggered inspection of 10% of assets each year.

d.	Cleaning of 30% of manhole and catch basin assets and 10% of pipe and culvert assets each year.

e.	Repair of 2% of assets each year.

f.	Rehabilitation of 23 catch basins and 21 pipes with a total length of 1500 feet.

g.	Replacement of 39 culverts, 23 catch basins, 21 pipes with a total length of 1500 feet, and 1 manhole. Includes cost estimates for the NE Union Hill Road @ 225th Ave NE box culvert ($1.35 M) and S 96th St stormwater pipes projects ($1.48 M).

Exhibit A

Summary of mapped and inspected assets by condition and recommended mitigation action in each map area

| Map Area Risk Exposure | Count of Assets | Percent of System Total |
| --- | --- | --- |
| Map Area 1: Kirkland Unincorporated | 58 | 6% |
| Critical | 1 | 0% |
| Immediate Preservation | 1 | 0% |
| High | 38 | 4% |
| Preservation Rehabilitation | 19 | 2% |
| Preservation Replacement | 5 | 1% |
| Enhanced Condition Assessment | 14 | 2% |
| Medium | 9 | 1% |
| Preservation Rehabilitation | 1 | 0% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 2 | 0% |
| Low | 10 | 1% |
| Status Quo | 10 | 1% |
| Map Area 2: Redmond Unincorporated | 183 | 20% |
| Critical | 2 | 0% |
| Enhanced Condition Assessment | 2 | 0% |
| High | 31 | 3% |
| Preservation Rehabilitation | 5 | 1% |
| Preservation Replacement | 2 | 0% |
| Enhanced Condition Assessment | 24 | 3% |
| Medium | 60 | 7% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 54 | 6% |
| Low | 90 | 10% |
| Status Quo | 90 | 10% |
| Map Area 3: Sammamish-Duval Unincorporated | 73 | 80% |
| Critical | 7 | 1% |
| Immediate Preservation | 5 | 1% |
| Enhanced Condition Assessment | 2 | 0% |
| High | 34 | 4% |
| Preservation Rehabilitation | 11 | 1% |
| Preservation Replacement | 6 | 1% |
| Enhanced Condition Assessment | 17 | 2% |
| Medium | 12 | 1% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 6 | 1% |
| Low | 20 | 2% |
| Status Quo | 20 | 2% |
| Map Area 4: I-90 Corridor | 82 | 9% |
| Critical | 3 | 0% |
| Immediate Preservation | 3 | 0% |
| High | 37 | 4% |
| Preservation Rehabilitation | 17 | 2% |
| Preservation Replacement | 5 | 1% |
| Enhanced Condition Assessment | 15 | 2% |
| Medium | 17 | 2% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 11 | 1% |
| Low | 25 | 3% |
| Status Quo | 25 | 3% |
| Map Area 5: White Center | 41 | 5% |
| Critical | 1 | 0% |
| Immediate Preservation | 1 | 0% |
| High | 17 | 2% |
| Preservation Rehabilitation | 10 | 1% |
| Preservation Replacement | 2 | 0% |
| Enhanced Condition Assessment | 5 | 1% |
| Medium | 12 | 1% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 6 | 1% |
| Low | 11 | 1% |
| Status Quo | 11 | 1% |
| Map Area 6: Renton-Tukwila | 58 | 6% |
| Critical | 2 | 0% |
| Immediate Preservation | 2 | 0% |
| High | 26 | 3% |
| Preservation Rehabilitation | 14 | 2% |
| Preservation Replacement | 5 | 1% |
| Enhanced Condition Assessment | 7 | 1% |
| Medium | 22 | 2% |
| Preservation Rehabilitation | 4 | 0% |
| Enhanced Condition Assessment | 5 | 1% |
| Status Quo | 13 | 1% |
| Low | 8 | 1% |
| Status Quo | 8 | 1% |
| Map Area 7: Lake Youngs | 100 | 11% |
| Critical | 7 | 1% |
| Immediate Preservation | 5 | 1% |
| Enhanced Condition Assessment | 2 | 0% |
| High | 35 | 4% |
| Preservation Rehabilitation | 8 | 1% |
| Preservation Replacement | 5 | 1% |
| Enhanced Condition Assessment | 22 | 2% |
| Medium | 25 | 3% |
| Preservation Rehabilitation | 2 | 0% |
| Enhanced Condition Assessment | 6 | 1% |
| Status Quo | 17 | 2% |
| Low | 33 | 4% |
| Status Quo | 33 | 4% |
| Map Area 8: Maple Valley | 117 | 13% |
| Critical | 4 | 0% |
| Immediate Preservation | 4 | 0% |
| High | 40 | 4% |
| Preservation Rehabilitation | 14 | 2% |
| Preservation Replacement | 9 | 1% |
| Enhanced Condition Assessment | 17 | 2% |
| Medium | 34 | 4% |
| Enhanced Condition Assessment | 11 | 1% |
| Status Quo | 23 | 3% |
| Low | 39 | 4% |
| Status Quo | 39 | 4% |
| Map Area 9: Auburn-Federal Way | 66 | 7% |
| Critical | 1 | 0% |
| Immediate Preservation | 1 | 0% |
| High | 15 | 2% |
| Preservation Rehabilitation | 2 | 0% |
| Enhanced Condition Assessment | 13 | 1% |
| Medium | 29 | 3% |
| Enhanced Condition Assessment | 4 | 0% |
| Status Quo | 25 | 3% |
| Low | 21 | 2% |
| Status Quo | 21 | 2% |
| Map Area 10: Auburn Unincorporated | 74 | 8% |
| High | 37 | 4% |
| Preservation Rehabilitation | 15 | 2% |
| Preservation Replacement | 9 | 1% |
| Enhanced Condition Assessment | 13 | 1% |
| Medium | 31 | 3% |
| Preservation Rehabilitation | 1 | 0% |
| Enhanced Condition Assessment | 9 | 1% |
| Status Quo | 21 | 2% |
| Low | 6 | 1% |
| Status Quo | 6 | 1% |
| Map Area 11: Skykomish | 7 | 1% |
| Critical | 2 | 0% |
| Immediate Preservation | 2 | 0% |
| High | 3 | 0% |
| Preservation Rehabilitation | 1 | 0% |
| Enhanced Condition Assessment | 2 | 0% |
| Medium | 2 | 0% |
| Status Quo | 2 | 0% |
| Map Area 12: Vashon Island | 33 | 4% |
| Critical | 3 | 0% |
| Immediate Preservation | 3 | 0% |
| High | 13 | 1% |
| Preservation Rehabilitation | 6 | 1% |
| Preservation Replacement | 4 | 0% |
| Enhanced Condition Assessment | 3 | 0% |
| Medium | 9 | 1% |
| Enhanced Condition Assessment | 3 | 0% |
| Status Quo | 6 | 1% |
| Low | 8 | 1% |
| Status Quo | 8 | 1% |
| Map Area 13: Lake Forest Park | 1 | 0% |
| High | 1 | 0% |
| Preservation Rehabilitation | 1 | 0% |
| Map Area 14: New Castle | 4 | 0% |
| High | 2 | 0% |
| Preservation Rehabilitation | 1 | 0% |
| Preservation Replacement | 1 | 0% |
| Medium | 2 | 0% |
| Preservation Rehabilitation | 2 | 0% |
| Grand Total | 897 | 100% |