Metropolitan King County Council

Utilities and Parks Committee

# CONSENT AGENDA STAFF REPORT

| AGENDA ITEM:: | 5 | DATE: | June 24, 2008 |
| --- | --- | --- | --- |
| PROPOSED NO.: | 2008-0004 | PREPARED BY: | Marilyn Cope |

SUBJECT 	 An ordinance approving the NE Sammamish Water and Sewer Plan.

SUMMARY

Proposed Ordinance 2007-0004 would approve the NE Sammamish Water and Sewer Plan.  Council approval of water utility comprehensive plans is required by county code as a prerequisite for operating in unincorporated King County, granting right of way construction permits, granting new or renewed franchises, and service boundary annexations.

The NE Sammamish Water and Sewer Plan is attached to Proposed Ordinance 2008-0004.  Fiscal, regulatory notes and the Utilities Technical Review Committee’s review are also included in the Executive’s transmittal.

BACKGROUND

King County Utility Comprehensive Plan Criteria

King County Code 13.24 requires Council approval of comprehensive plans for water utilities as a prerequisite for operating in unincorporated, receiving county approval for annexations, or receiving county right-of-way franchises and construction permits.  In accordance with RCW 43.20.260, approval of comprehensive water plans also provides the determination to state regulatory agencies, that the plan is consistent with the King County Comprehensive Plan and related policies and implementing development regulations.

King County Code 13.24 also requires the Utilities Technical Review Committee (UTRC) to review and make recommendations to the Executive and County Council on the adequacy of all water system comprehensive plans and related matters, and to determine whether the plan:

- is consistent with local comprehensive plans;

- is consistent with the King County Comprehensive Plan;

- reflects current water supply and demand;

- forecasts future water supply and demand;

- provides a capital plan for obtaining, using, storing and conveying water;

- provides sufficient information to demonstrate the utility district’s ability to provide service consistent with all applicable laws and regulations.

ANALYSIS

NE Sammamish Water and Sewer District

The NE Sammamish Water and Sewer District (the District) was created in 1969 as the Sahalee Sewer District, and has expanded and changed its name as that part of King County has become developed.  The District currently provides sewer service in general within the incorporated area of the city of Sammamish.  It has separate agreements with the city of Redmond and the Sammamish Plateau Water and Sewer District for the provision of sewer service, and the conveyance of wastewater to the metropolitan King County system.  The District also has agreements to provide service outside the Urban Growth Area (UGA) to four schools, which will ultimately be provided service by the city of Redmond.  The total area served is approximately 2400 acres, most of which is already serviced, with the remainder to be served as development infill.  The estimated population served within the District’s boundaries is 13,500 people, and 4,580 equivalent residential units (ERUs).  The projected population at build-out is 14,700, which the District expects to achieve between 2020 and 2030.

The District’s sewer service area includes the Evans Creek Valley, which is outside the UGA.  Current zoning restricts service to this area, consistent with the King County Comprehensive Plan.

The system currently has 15 collection basins, with 59 miles of sewer pipe and nine lift stations.  It has no treatment facilities—all wastewater is delivered to the regional system.  The system’s facilities are generally new—no pipeline is older than 35 years—and is in generally good condition.

System Infrastructure

As part of the development of the Plan, the District reviewed pipeline integrity, infiltration and inflow, pipeline capacity, lift stations, telemetry and control system, and wastewater quality analysis.  The recommendations that the District intends to pursue are:

- Implementation of a video inspection program for periodic inspection of the oldest areas of the system in order to anticipate and avoid problems.

- The calculated rates of infiltration and inflow at peak storm events (a maximum of 685 gallons per acre per day) are substantially below the King County maximum rate of 1100 gallons per acre per day, largely due to the District’s construction and testing standards, and sufficient capacity in the stormwater system.  The District will investigate areas prone to flooding and implement waterproofing of manhole covers.

- The system currently has adequate pipeline capacity for anticipated growth.  Several sections of the existing system are expected to be over capacity at full development, and the sections will have to be replaced with larger pipe, as identified in the District’s Capital Improvement Program (CIP).

- The District has recently replaced or retrofitted its lift stations in order to gain higher capacity and additional emergency storage.  The older pumps and motors have been replaced or are scheduled for replacement.

- The District recently replaced its telemetry system with a PC-based system with programmable telemetry units at each lift station, which allows central monitoring of the system from either the District’s office of from employee homes via the internet.

- The District had a significant corrosion and odor problem downstream of one of its lift stations, which has been remedied by chemical treatment and retrofitting of the manholes damaged by corrosion.

Financial Plan

The CIP through 2012 includes six improvements with a total cost of $947,000.  The improvements will be funded through operating reserve transfers and low interest rate loans, or through bond sales.

The District anticipates increasing its portion of the monthly sewer charge to its customers by three percent per year from the 2005 rate of $19.45/per month.

Conservation and Reclamation

The District incorporated into its planning anticipated investments in water conservation by the water utilities within the District’s service area.

The District does not have any treatment facilities, and is required to deliver its wastewater flows to the regional wastewater system.  For that reason, it does not anticipate delivering reclaimed water to any potential customers.  It has identified the Sahalee golf course as a potential user of reclaimed water, should it become available for outdoor irrigation.

State Environmental Policy Act (SEPA)

The Utility’s Board of Directors conducted a public hearing on a proposed Determination of Nonsignificance (DNS) for the Plan under SEPA on September 6, 2007, and adopted the DNS.

UTRC Review

The NE Sammamish Water and Sewer Plan was reviewed by the UTRC and found to meet the requirements of King County Code 13.24.  The UTRC has recommended approval of the plan.

ATTACHMENTS

1.  Proposed Ordinance 2008-0004 with attachments

2.  Transmittal letter, December 20, 2007

3.  Fiscal note

4.  Regulatory note

5.  Review matrix