| Review of King County Water District No. 111 2007 Water Comprehensive Plan |
| --- |
|  | A. General and water and sewer plan: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | Applicable to special purpose districts (Title 57 Revised Code of Washington (RCW)) and water utilities distributing or obtaining water in unincorporated King County. | King County Water District No. 111’s (District) 2007 Water Comprehensive Plan (Plan) is subject to King County Council approval pursuant to RCW 57.16.010(6). The District obtains and distributes water in part in unincorporated King County. Therefore, King County Code (KCC) 13.24 applies. |
| (2) | Consistency with King County Comprehensive Plan and Development regulations, and policies including KCC 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development. | The District’s Plan is consistent except as noted. The District’s water franchise, number 12021, was approved in November 1995 and expires in November 2020. The franchise covers the District’s entire Retail Water Service Area (RWSA). |
| (3) | Infrastructure for existing and future service areas based on adopted land use map. | Yes. The District used adopted King County land use maps. The Plan was reviewed by King County Department of Transportation and the Department of Development and Environmental Services (DDES). |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement. | The RWSA is within the planning area identified in the South King County Coordinated Water System Plan (CWSP). The corporate boundaries of the District are smaller still, but the District is authorized to provide service to parcels within the RWSA. The RWSA includes portions of the cities of Auburn, Covington, Kent, and unincorporated King County. Several of the unincorporated parts of King County in the RWSA are slated for eventual annexation by one of the adjacent cities. The District does not foresee its boundaries growing beyond those specified as its planning area in the South King County CWSP. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | The District currently obtains its water from a combination of wells and purchases from the city of Auburn. The projected maximum day demand in 2028 is approximately 4.81 million gallons per day, which will be met with continued use of the wells and additional purchases, including purchases from Tacoma. With the added supply from Tacoma, the District’s water supplies appear more than sufficient to meet projected maximum day demand in 2028. |
| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved CWSP. | The Plan is currently consistent with the South King County CWSP for the service area, with its RWSA being the same as the planning area identified in the South King County CWSP. The Plan discusses the conservation program goals for the South King County CWSP, but notes that no goals were established beyond the year 2000. Since then, the District has maintained its existing program and added additional elements it deemed necessary and appropriate to meet its commitment to conserve water. The District has met and exceeded its conservation targets for the last several years. The District is continuing to implement its current Water Use Efficiency Program, which will meet Washington State Department of Health (DOH) efficiency requirements under the Municipal Water Law. |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | State and local health requirements. | Yes. |
| (8) | Creation and maintenance of logical service areas. | Yes, the service area is logical. The District’s boundaries are fairly well fixed, although its corporate boundaries might be changed to be consistent with its RWSA boundaries. |
| (9) | Elimination or prevention of duplicate facilities. | Yes. The District will consider allowing a satellite water system if the proposed system is more than 1,320 feet beyond an existing water main. The District has adopted satellite management policies and is approved as a Satellite Management Agency (SMA) by DOH. The District has entered into agreements with neighboring water utilities about their respective service areas. |
| (10) | Promotion of most healthful and reliable services to the public. | Yes. A hydraulic analysis performed for the District shows that, with the addition of proposed improvements, the District’s water distribution system has sufficient capacity to meet peak day and peak hour demand through the six- and 20-year planning periods. The hydraulic analysis of the District’s system indicates some areas where water main pressures will be high, requiring some homeowners to install pressure reducing valves. In the 2013 analysis, the system does not meet fire flow criteria for part of the southwest portion of the District, but with the connection to the Tacoma system and associated piping, that problem will be resolved. Fire flow was adequate for the whole system in the 2028 analysis. Water purveyed by the District is evaluated for compliance with water quality standards and results indicate the District complies with the standards. |
| (11) | Provision of service at a reasonable cost, and maximization of use of public facilities. | The District’s rates for water service are comparable to the rates charged by similar utilities. The District has a graduated rate structure to encourage efficiency of water use during the summer months. |
| (12) | King County Comprehensive Plan and other pertinent county adopted plans and policies. | Yes, there is consistency between the District’s Plan and the King County Comprehensive Plan, except as noted herein. |
| (13) | Basin-wide or multibasin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (DOE) or DOH. | The District is a charter member of the South King County Regional Water Association and an active member of the Washington Association of Sewer and Water Districts. The District does not provide sewer services. All wastewater produced within the service area of the District is either treated by on-site systems or collected by other utilities. The Plan is consistent with the South King County CWSP, except as noted. |
| (14) | Applicable state water quality, water conservation, and waste management standards. | The District tests the water produced from its wells and the water meets all water quality standards. The District’s water use per Equivalent Residential Unit (ERU) has dropped since 1997 from 255 to 220 gallons per day (gpd), an improvement over projected per ERU use of 236 gpd. This indicates that the District has been successful in reducing water use through its conservation activities. Although the District is projecting lost and/or unaccounted-for water at ten percent for planning purposes, it has run below that in recent years. The District intends to meet its conservation goal of one percent per year usage reduction per ERU through 2017. The District participated in the regional conservation program through the South King County Regional Water Association, but that program was discontinued in 2000. The District currently participates in the Puget Sound Water Conservation Coalition. |

| (15) | Water Resources Act (RCW 90.54). | The District supplemented the Plan with a brief evaluation of its conservation program from a cost effectiveness perspective. The Plan makes no connection between the District’s conservation program and the requirements of RCWs 90.54.180 and 90.03.386. The District will maintain its existing conservation (efficiency) program while complying with DOH’s Water Use Efficiency Rule. |
| --- | --- | --- |
| (16) | Growth Management Act (GMA) (RCW 36.70A). | The District assessed the population targets from the Growth Management Planning Council while using Puget Sound Regional Council data in forecasting future water demand and affirmed they can meet the needs forecasted under the Growth Management Act. Since the District includes unincorporated areas, it appropriately used the land use zoning of King County for those areas. |
| (17) | Ground water Management Plans. | There is a ground water management plan for South King County, but the District’s Plan makes only brief mention of that plan in relationship to its wells. The plan was developed by the South King County Regional Water Association. The District’s Plan briefly discusses a Wellhead Protection Program that was developed in 1997 for its wells but does not include it (the plan is available at the District’s office). The Plan does include a 2005 Hazard Inventory Update, which is, in part, an update to the Wellhead Protection Program. |
| (18) | Federally approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | The District’s water comes in large part from wells located within the Green River Basin, which is the subject of salmon recovery efforts. However, the Plan makes only passing mention of those efforts (see 19 below). |
| (19) | Requirements for salmon recovery under chapter 77.85 RCW, and other plans, including regional water supply or water resource management plans. | The District participates indirectly in salmon recovery planning for Water Resource Inventory Area 9 through its membership in the South King County Regional Water Association and the Washington Association of Sewer and Water Districts. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | The District does not provide wastewater collection and treatment for its customers. The District is, however, willing to consider or participate in appropriate water reuse projects. The District completed the reclaimed water checklist provided by DOH as required by chapter 90.46 RCW. The Plan identified a number of locations where reclaimed water might be used if it were available. However, it does not appear the use of reclaimed water is feasible in the near term within the District. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | Not applicable. |
| (22) | FW-12(c): ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Sufficient water supply for projected growth is available. No apparent linkages and little relevance of the Plan to fish habitat needs. |
| (23) | CA-5 and CA-6: adopt policies to protect quantity and quality of ground water. | There is a South King County Ground Water Management Plan, but the District’s Plan mentions it only in passing. However, the District is quite concerned about protection of its ground water resources. See comment number 17 for information about the District’s wellhead protection program. |
| (24) | CO-5: water supply shall be regionally coordinated. | The District took part in the South King County CWSP process and is a member of the South King County Regional Water Association. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The District is implementing the water use efficiency program required by DOH. |
| (26) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users. | The District identified a number of sites where reclaimed water could be used. The District, while not producing reclaimed water itself, is willing to consider appropriate projects for the use of reclaimed water. See number 20 above. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (27) | E-434: management and protection of water resources by King County through incentives, regulations and programs. | Yes. |
| (28) | E-468: protect ground water, and develop strategies to compensate or mitigate for losses. | See comments 17 and 23. |
| (29) | E-477: protect and enhance surface waters, including Puget Sound. | Not applicable. Protection of Puget Sound and its tributary streams could possibly be enhanced by reduction of demand or using alternative sources of water, such as reclaimed water. |
| (30) | E-606: protect critical habitat. | Not applicable. |
| (31) | F-102: King County will provide or manage countywide services, which include wastewater, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands. | Yes, for those portions of the District’s service area that are unincorporated. Much of the District’s service area is slated for eventual incorporation. |
| (32) | F-104: plan for provision of services to rural areas. | Yes. The District provides water service in rural areas consistent with the King County Comprehensive Plan. The District recognizes the rural nature of portions of its service area and has no plans for the provision of sewer service. |
| (33) | F-105: King County work with cities and service providers to provide services. | The CIP program is appropriately focused and adequate. |
| (34) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA. | Applicable only with respect to water from Tacoma’s Second Supply Project. Managers of that project are working to comply with ESA provisions and requirements. |
| (35) | F-202: ensure adequate supply of public facilities to support communities. | Yes, although there are some pressure issues within the District. Connection to Tacoma’s Second Supply Project should resolve those issues. |
| (36) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | Yes. The District has agreements with all adjacent purveyors. |
| (37) | F-208: support rural levels of development and not facilitate urbanization. | Yes. See comment 32. |
| (38) | F-209: capital facility plans and improvement programs for services to unincorporated King County are consistent with King County Comprehensive Plan. | Yes. The District’s CIP is consistent with the King County Comprehensive Plan. |
| (39) | F-210: King County helps coordinate development of utility facilities. | The District has postponed some of its CIP projects pending such coordination. |
| (40) | F-212: King County CIP shall show that projected need for services and facilities in the Urban Growth Area (UGA) can be met in compliance w/concurrency requirements of the GMA. | The District’s CIP is intended to meet the needs of its entire service area, including both the urban and rural portions. |
| (41) | F-213: water and sewer utilities providing service to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and the King County Code. | The District’s CIP for those parts of its service area that are rural in nature and unincorporated is reasonable and consistent with GMA and the King County Comprehensive Plan. |
| (42) | F-215: King County shall initiate a sub-area planning process with any service provider that declares, in capital facilities plan, an inability to meet service needs within service area. | Not applicable. The District did not identify any inability to meet service needs within its service area. |
| (43) | F-217: where an area-wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | No area-wide water or sewerage deficiency identified. |
| (44) | F-225: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs. | The District purchases some of its water from Auburn and will soon be purchasing water from Tacoma as well. It also facilitates wheeling of water to other utilities. |
| (45) | F-226: Group A water systems must meet duty to serve requirement within service area as defined under CWSP or by individual water system plans. | See comments 4 and 5. |
| (46) | F-227-231: provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers. | The District recognizes its duty to serve within its service area. The District is an approved SMA for purposes of operating small water systems within its service area. |

| (47) | F-232: service from exempt wells limited to subdivisions with no more than six lots, and limited to one well unless an additional well is needed for flow requirements for the six lots; water from the exempt well is limited to no more than one-half acre irrigation. | The District has an appeals process if an applicant contends that the District cannot provide water in a timely and reasonable manner. |
| --- | --- | --- |
| (48) | F-234-236: develop regional water supply plan with a role for reclaimed water as a source of supply. | See comment 20. |
| (49) | F-237: King County supports the use of interties consistent with planning, and implement approved ESA and Clean Water Act (CWA) response requirements. | The District already uses interties to obtain some of its supply and to provide water to adjacent utilities. |
| (50) | F-239: King County partner with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | King County is willing to work with the District on these issues, particularly the provision of water service in unincorporated areas at an affordable price and the use and evaluation of reclaimed water opportunities. |
| (51) | F-240: Utilities Technical Review Committee (UTRC) to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for ground water, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | The UTRC did consider the given issues and recommends approval of the Plan. |
| (52) | F-241: in reviewing proposals for modified and expanded service area boundaries, UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | The District is not proposing to alter its service area boundaries. |
| (53) | F-242: UTRC to develop a water accounting system, in conjunction with water utilities, to ensure the ability of utilities to issue certificates of availability. | The District uses the water availability certificate document to demonstrate water availability for DDES. |
| (54) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | Not applicable. The District’s storage facilities are all tanks. |
| (55) | F-244: ground water supplies should be protected by preventing land uses that may adversely affect quantity or quality. | See comments 5 and 17 for wellhead protection program comments. |