| UTRC Review of the King County Water District No. 49 2008 Water System Plan |
| --- |
| A review of the specific statutes, rules, codes, and policies to the water system plan is as follows: |
|  | A. General and water and sewer plan: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | Review is applicable to special purpose districts organized under Title 57 Revised Code of Washington (RCW). Is there a need to meet the consistency requirements of RCW 43.20.260? | Yes, the King County Water District No. 49’s (District) 2008 Water System Plan (Plan) is subject to King County Council approval under Title 57 RCW. The Washington State Department of Health (DOH) also needs to demonstrate consistency for the Plan under RCW 43.20.260. The District self-certified consistency with the City of SeaTac’s comprehensive plan. The cities of Normandy Park and Burien affirmed consistency between their comprehensive plans and the plan of the water district. |
| (2) | Consistency with King County Comprehensive Plan and Development regulations, and policies including King County Code (KCC) 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development. | Yes, the District’s 2008 Plan is consistent. |
| (3) | Infrastructure for existing and future service areas based on adopted land use map. | Not applicable. The District’s service area includes only lands within the incorporated cities of Burien, Normandy Park, and SeaTac. |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement. | Not applicable. The District’s service area is well defined, as the District is bounded on all sides by other water utilities. The service area has not changed recently and is not expected to change. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | Yes, the Plan demonstrates an ability to provide service consistent with applicable statutes, codes and regulations. The District obtains its water from Seattle Public Utilities (SPU) through its Cedar and Tolt River distribution mains. The projected daily demand in 2030 is approximately 1.45 million gallons per day (mgd) without conservation and 1.38 mgd with conservation. |

| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved Coordinated Water System Plan (CWSP). | The District is not in an area covered by a CWSP. The District is participating, along with Seattle and other water utilities, in the Saving Water Partnership with the regional goal of per capita savings of one percent per year between 2000 and 2010. The District’s water use efficiency plan is organized to conform to the requirements of the Water Use Efficiency Rule. |
| --- | --- | --- |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | State and local health requirements. | Yes. |
| (8) | Creation and maintenance of logical service areas. | Yes, the service area is logical. |
| (9) | Elimination or prevention of duplicate facilities. | Yes. The District intends to provide service within its service area by means of direct connection. The District does not foresee any need to provide satellite management services, since direct service is available throughout its service area. The District has entered into agreements with neighboring water utilities (King County Water District No. 20 and Highline Water District) to provide emergency supplies through interties. |
| (10) | Promotion of most healthful and reliable services to the public. | Yes. A hydraulic analysis performed for the District shows that the District has some storage problems. The District is looking at ways to remedy those problems. The hydraulic analysis of the District’s system identifies the need for improvements to the distribution system, particularly the replacement of undersized water mains to improve pressure and velocity conditions. If the capital improvement plan (CIP) is fully implemented, the District’s water distribution system should have sufficient capacity to meet peak day and peak hour demand throughout the six- and 20-year planning periods. The District’s contract for water from SPU expires in 2011, so a new contract will need to be negotiated. Water purveyed by the District complies with public health standards. |
| (11) | Provision of service at a reasonable cost, and maximization of use of public facilities. | Yes, the District’s rates for water service are comparable to the rates charged by similar utilities. The District just raised its rates for the first time in ten years. The District has adopted a graduated rate structure to encourage efficiency of water use. |
| (12) | King County Comprehensive Plan and other pertinent county adopted plans and policies. | Yes, there is consistency between the District’s Plan and the King County Comprehensive Plan. |
| (13) | Basin-wide or multibasin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (Ecology) or DOH. | The District has not been involved in multibasin water plans, although it does take part in SPU initiatives. The District neither collects nor treats wastewater. |
| (14) | Applicable state water quality, water conservation, and waste management standards. | Yes, applicable standards are met. The District receives treated water from SPU which does all the testing. The District does coliform monitoring in keeping with SPU’s guidelines. The District’s water use per equivalent residential unit (ERU) in 2007 was 176 gallons per day. The District is using DOH’s equation to calculate maximum day demand at twice the average day demand. The District’s conservation activities should reduce the peaking number. The District’s distribution system loss (non-revenue or unaccounted-for water) has generally been less than six percent in recent years, although that number may be low due to underreporting by meters that have subsequently been replaced. The District is committed to staying below the ten percent standard in the Water Use Efficiency Rule. The District is participating in the Saving Water Partnership’s regional effort to save 11 mgd between 2000 and 2010, and another 15 mgd by the year 2030. |

| (15) | Water Resources Act (RCW 90.54). | The District has had a conservation program in place since the early 1990s. The District’s Water Use Efficiency Plan is organized to conform to the requirements of the Water Use Efficiency Rule adopted by DOH. The Plan makes no connection with the requirements of RCW 90.54.180, although the date of the District’s program would seem to indicate a connection. The Plan does not mention the provisions of RCW 90.03.386. |
| --- | --- | --- |
| (16) | Growth Management Act (GMA) (RCW 36.70A). | Yes, the District affirms they can meet the population target policies from the Growth Management Planning Council for the three cities served. The six-year portion of the CIP identifies public money they may need for capital facilities. |
| (17) | Ground water management plans. | Not applicable. The District receives all of its water supply from SPU. |
| (18) | Federally approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | Not applicable. Seattle has a Habitat Conservation Plan for its Cedar River watershed, the source of the District’s supply. |
| (19) | Requirements for salmon recovery under Ch. 77.85 RCW, and other plans, including regional water supply or water resource management plans. | Not applicable. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW and CO-7. | The Plan includes a brief evaluation of opportunities for the use of reclaimed water. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | Not applicable. |

| (22) | FW-12(c): ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Yes, sufficient water supply for projected growth is available. There is no apparent linkage and little relevance of the Plan to fish habitat needs (SPU’s Plan would address that situation.). |
| --- | --- | --- |
| (23) | CA-5, CA-6, and E-434 and policies to protect quantity and quality of ground water. | Not applicable. The District does not use ground water. |
| (24) | CO-5: water supply shall be regionally coordinated. | Yes, the District’s supply is regionally coordinated, since it purchases its water from SPU. Also, apart from its agreement with SPU for its main water supply, the District also has agreements with neighboring water systems (King County Water District No. 20 and Highline Water District) for emergency supplies. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The District has organized its conservation program to conform to the requirements of the water use efficiency program rule adopted by DOH. The District also participates in SPU’s Saving Water Partnership along with 16 other water utilities. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (26) | F-102: King County will provide or manage countywide services, which include wastewater, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands. | Yes, although the District’s service area does not include any areas that are unincorporated. |
| (27) | F-104: plan for provision of services to rural areas. | Not applicable. The District just provides water to parts of three cities. |
| (28) | F-105: King County to work with cities and service providers to establish priority areas for public funding of capital facilities. | The CIP is adequate and appropriately focused. |
| (29) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA. | Yes. |
| (30) | F-202: ensure adequate supply of public facilities to support communities. | Yes, the District has sufficient water supplies and has an arrangement for emergency supply from adjacent utilities. |

| (31) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | Yes. |
| --- | --- | --- |
| (32) | F-208: support rural levels of development and not facilitate urbanization. | Not applicable. The District service area is entirely within the Urban Growth Area (UGA). |
| (33) | F-209 and F-212: capital facility plans and improvement programs for services to unincorporated King County are consistent with the King County Comprehensive Plan. | Yes, the CIP is consistent with the King County Comprehensive Plan. The District’s service area does not include any unincorporated lands. |
| (34) | F-210: King County helps coordinate development of utility facilities. | Yes, to the extent applicable, King County will do this. |
| (35) | F-215: King County shall initiate a sub-area planning process with any service provider that declares, in its capital facilities plan, an inability to meet service needs within service area. | Not applicable. The District did not identify any inability to meet service needs within its service area. |
| (36) | F-217: where an area-wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | No area-wide water deficiency is identified. |
| (37) | F-225: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs. | The District has agreements with three of its neighboring utilities for purchases of water for both primary supply (SPU) and on an emergency basis (Water District No. 20 and Highline Water District). |
| (38) | F-226: Group A water systems must meet duty to serve requirement within service area as defined under CWSP or by individual water system plans. | Yes, the District is committed to meeting its duty to serve, even though it is not in a CWSP area. Also see comments 4 and 5. |
| (39) | F-227-231: provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers. | The District recognizes its duty to serve within its service area and is committed to providing water to all its customers within its service area by direct connection. Since it can provide water by direct connection, the District sees no need to consider providing satellite management services. There are no other Group A public water systems within the District’s service area. |
| (40) | F-237: King County supports the use of interties consistent with planning, and implementation of approved ESA and Clean Water Act response requirements. | The District is supplied through connection to SPU’s distribution system. The District also has emergency interties with King County Water District No. 20 and the Highline Water District. |
| (41) | F-239: King County partners with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | King County is willing to work with the District on these issues, particularly the evaluation of reclaimed water opportunities. |
| (42) | F-240: Utilities Technical Review Committee (UTRC) to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for ground water, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | The UTRC did consider the given issues and recommends approval of the Plan. |
| (43) | F-241: in reviewing proposals for modified and expanded service area boundaries, the UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | The District is not changing its service area and really cannot expand as all surrounding areas are served by other purveyors. The Plan states that the District would likely only alter its service area boundaries through interlocal agreements with another utility. A merger between systems is a remote possibility, but none is contemplated at present. |
| (44) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | Not applicable. The District’s storage facilities are tanks. |
| (45) | F-244: ground water supplies should be protected by preventing land uses that may adversely affect quantity or quality. | Not applicable. The District’s supplies come entirely from surface water sources. |